## Overview
Chiller Plant
Data export · 2026-06-09 → 2026-07-13 · 35 days · 299 readings · generated 2026-07-18 02:09
PEAK PLANT LOAD | PEAK %RLA | AVG COND ΔT | DAYS LOGGED
465 | 99.8 | 6.1 | 35
READINGS | PEAK COND ΔT
299 | 8
Tabs → 📈 Plant Load · %RLA are view-only charts; Readings / Daily hold the data.

## Readings
Date | Slot | Chiller | Set Pt | CHW Lv | CHW Ent | Tons | Cond Lv | Cond Ent | RLA % | Evap Appr | Cond Appr | CHW Pump | Cond Pump | Notes
2026-06-09 | 6AM | 1 | 45 | 49.7 | 54.5 | 119.4 | 83.4 | 79.8 | 45.5 | 1.3 | 1.7 | ALL | ALL | Started #1 chiller @ 6:15pm
2026-06-09 | 8AM | 1 | 45 | 45 | 53 | 199 | 87 | 81 | 65 | 1.7 | 1.8 | All | All
2026-06-09 | 4PM | 1 | 45 | 45 | 54 | 223.9 | 93.6 | 86.7 | 78.4 | 1.9 | 1.8 | 5 | 6
2026-06-09 | 10PM | 1 | 45 | 45 | 53.9 | 221.4 | 91.5 | 84.5 | 74.6 | 1.8 | 2 | 5 | 6
2026-06-09 | 12AM | 2 | 45 | 45 | 53 | 199 | 88.2 | 78.8 | 67.8 | 2.1 | 0.4 | 6 | 5
2026-06-09 | 6AM | 2 | 45 | 45.1 | 56.6 | 286.1 | 91.2 | 77.8 | 69.8 | 2.6 | 2 | 6 | 5
2026-06-09 | 8AM | 2 | 45 | 45 | 52 | 174.1 | 89 | 82 | 73 | 2.3 | 0.6 | 6 | 5
2026-06-09 | 2PM | 2 | 45 | 45 | 53.8 | 218.9 | 95 | 86.8 | 88 | 2.5 | 0.7 | 6 | 5
2026-06-09 | 4PM | 2 | 45 | 45 | 53.8 | 218.9 | 95 | 86 | 88 | 2.5 | 0.7 | 6 | 5
2026-06-09 | 10PM | 2 | 45 | 45 | 53.8 | 218.9 | 95 | 86 | 86 | 2.5 | 0.8 | 6 | 5
2026-06-10 | 12AM | 1 | 45 | 45 | 52.3 | 181.6 | 85 | 79.6 | 59.8 | 1.5 | 1.8 | Both | Both
2026-06-10 | 6AM | 1 | 45 | 45 | 52.8 | 194 | 87.4 | 81.6 | 64.6 | 1.4 | 1.8 | Both | Both
2026-06-10 | 8AM | 1 | 45 | 45.1 | 53.3 | 204 | 89.3 | 82.9 | 70.5 | 1.8 | 1.9 | Both | Both
2026-06-10 | 2PM | 1 | 45 | 45 | 54.2 | 228.9 | 93.5 | 86.2 | 80.4 | 2 | 1.9 | Both | Both
2026-06-10 | 4PM | 1 | 45 | 45 | 54.4 | 233.8 | 95.3 | 87.8 | 83 | 2 | 1.8 | Both | Both
2026-06-10 | 10PM | 1 | 45 | 45 | 53.5 | 211.4 | 89.7 | 83.1 |  | 1.9 | 1.9 | Both | Both
2026-06-10 | 12AM | 2 | 45 | 45 | 51.1 | 151.7 | 85.7 | 77.8 | 61 | 1.9 | 0.4 | Both | Both
2026-06-10 | 6AM | 2 | 45 | 45 | 52.7 | 191.5 | 89.4 | 81.7 | 70.7 | 2.1 | 0.5 | Both | Both
2026-06-10 | 8AM | 2 | 45 | 45 | 53.2 | 204 | 90.8 | 83 | 73.8 | 2.1 | 0.6 | Both | Both
2026-06-10 | 2PM | 2 | 45 | 45 | 54.1 | 226.4 | 95.6 | 86.5 | 86.5 | 2.5 | 0.6 | Both | Both
2026-06-10 | 4PM | 2 | 45 | 45 | 54.3 | 231.3 | 97 | 88 | 90 | 2.6 | 0.7 | Both | Both
2026-06-10 | 10PM | 2 | 45 | 45 | 53.4 | 208.9 | 91.6 | 83.2 | 75.6 | 2.2 | 0.7 | Both | Both
2026-06-11 | 12AM | 1 | 45 | 45 | 52.5 | 186.6 | 85.4 | 79.6 | 61.8 | 1.6 | 1.9 | 6,6A | 5,5A
2026-06-11 | 6AM | 1 | 45 | 45 | 52 | 174.1 | 83.1 | 77.8 | 57.4 | 1.6 | 1.9 | 6,6A | 5,5A
2026-06-11 | 8AM | 1 | 45 | 44.9 | 52.4 | 186.6 | 85.4 | 79.8 | 62.6 | 1.6 | 1.9 | Both | Both
2026-06-11 | 2PM | 1 | 45 | 45.1 | 53 | 196.5 | 88 | 81.7 | 67.9 | 1.8 | 1.9 | Both | Both
2026-06-11 | 4PM | 1 | 45 | 45 | 52.9 | 196.5 | 88.1 | 82 | 67.1 | 1.8 | 1.9 | Both | Both
2026-06-11 | 10PM | 1 | 45 | 45 | 52.2 | 179.1 | 86.9 | 81 | 64.2 | 1.7 | 1.8 | Both | Both
2026-06-11 | 12AM | 2 | 45 | 45 | 52.4 | 184.1 | 87.3 | 80.1 | 63.8 | 2 | 0.4 | 6,6A | 5,5A
2026-06-11 | 6AM | 2 | 45 | 45 | 51.8 | 169.1 | 84.3 | 77.8 | 56.7 | 1.8 | 0.4 | 6,6A | 5,5A
2026-06-11 | 8AM | 2 | 45 | 45 | 52.3 | 181.6 | 86.8 | 79.9 | 62.3 | 2 | 0.4 | Both | Both
2026-06-11 | 2PM | 2 | 45 | 45 | 52.9 | 196.5 | 89.6 | 81.9 | 70.1 | 2.1 | 0.4 | Both | Both
2026-06-11 | 4PM | 2 | 45 | 45 | 52.7 | 191.5 | 87.7 | 82.2 | 67.2 | 2.1 | 0.4 | Both | Both
2026-06-11 | 10PM | 2 | 45 | 45 | 52.1 | 176.6 | 88.2 | 81 | 65.1 | 2.1 | 0.5 | Both | Both
2026-06-12 | 12AM | 1 | 45 | 45 | 52.2 | 179.1 | 86.7 | 80.8 | 63.6 | 1.7 | 1.8 | 6,6A | 5,5A | OFF @ 9:50am
2026-06-12 | 6AM | 1 | 45 | 45 | 51.8 | 169.1 | 82.5 | 77.3 | 58.1 | 1.5 | 1.9 | 6,6A | 5,5A
2026-06-12 | 8AM | 1 | 45 | 45 | 50.8 | 144.3 | 82.9 | 78.5 | 53.1 | 1.3 | 1.9 | Both | Both
2026-06-12 | 12AM | 2 | 45 | 45 | 51.9 | 171.6 | 87.9 | 80.9 | 63.7 | 1.9 | 0.5 | 6,6A | 5,5A | Cycled @ 8:41a
2026-06-12 | 6AM | 2 | 45 | 45 | 51.7 | 166.7 | 84 | 77.6 | 54.9 | 1.8 | 0.4 | 6,6A | 5,5A
2026-06-12 | 8AM | 2 | 45 | 44.9 | 50.6 | 141.8 | 83.1 | 78.1 | 48.6 | 1.5 | 0.7 | Both | Both
2026-06-12 | 2PM | 2 | 45 | 45 | 52.4 | 184.1 | 85.2 | 77.8 | 74 | 2.5 | 0.7 | 6A | 5
2026-06-12 | 4PM | 2 | 45 | 45 | 52.7 | 191.5 | 85.6 | 78.1 | 77 | 2.6 | 0.7 | Both | Both
2026-06-12 | 10PM | 2 | 45 | 45 | 50.9 | 146.8 | 79.5 | 73.7 | 54 | 1.9 | 0.6 | 6,6 | 5,5
2026-06-13 | 12AM | 2 | 45 | 45 | 50.9 | 146.8 | 78.4 | 73.7 | 54.7 | 2 | 0.6 | 6A | 5
2026-06-13 | 6AM | 2 | 45 | 45 | 50.8 | 144.3 | 79.1 | 73.5 | 52.6 | 1.9 | 0.5 | 6,6A | 5
2026-06-13 | 8AM | 2 | 45 | 45 | 53.3 | 206.5 | 88.6 | 80.5 | 86.2 | 2.8 | 1 | 6A | 5
2026-06-13 | 2PM | 2 | 45 | 45 | 52.6 | 189.1 | 87.6 | 80.1 | 79.1 | 2.5 | 0.8 | 6A | 5
2026-06-13 | 4PM | 2 | 45 | 45 | 52.4 | 184.1 | 88 | 80.6 | 77 | 2.5 | 0.8 | 6A | 5
2026-06-13 | 10PM | 2 | 45 | 45 | 52.3 | 181.6 | 87.1 | 79.9 | 75 | 2.5 | 0.7 | 6A | 5
2026-06-14 | 12AM | 2 | 45 | 45 | 51 | 149.2 | 82.2 | 76.4 | 58.2 | 2 | 0.6 | 6A | 5
2026-06-14 | 6AM | 2 | 45 | 45 | 53.5 | 211.4 | 84.8 | 81.7 | 88.3 | 2.8 | 1 | 6A | 5
2026-06-14 | 8AM | 2 | 45 | 45 | 53.7 | 216.4 | 91 | 82.6 | 92.3 | 0.9 | 1 | 6A | 5
2026-06-14 | 2PM | 2 | 45 | 45 | 51.7 | 166.7 | 83.5 | 76.5 | 69.4 | 2.4 | 0.7 | 6A | 5
2026-06-14 | 4PM | 2 | 45 | 45 | 51.4 | 159.2 | 82.2 |  | 66 | 2.4 | 0.7 | 6A | 5
2026-06-14 | 10PM | 2 | 45 | 45 | 50.3 | 131.8 | 81.7 | 75.9 | 55 | 2 | 0.3 | 6A | 5
2026-06-15 | 12AM | 2 | 45 | 51.8 | 54.8 | 74.6 | 76.1 | 73.7 | 37.4 | 1.5 | 0.6 | 6A | 5
2026-06-15 | 6AM | 2 | 45 | 52.1 | 55 | 72.1 | 75.8 | 73.2 | 30.5 | 1.6 | 0.7 | 6A | 5
2026-06-15 | 8AM | 2 | 45 | 44.7 | 48.7 | 99.5 | 80.3 | 75.3 | 44.8 | 1.6 | 0 | 6 | 5
2026-06-15 | 2PM | 2 | 45 | 45 | 49.3 | 107 | 83.8 | 79.7 | 51.5 | 1.7 | 1.1 | 6 | 5
2026-06-15 | 4PM | 2 | 45 | 45 | 49.5 | 111.9 | 83.6 | 75.2 | 52.3 | 1.8 | 1.3 | 6 | 5
2026-06-15 | 10PM | 2 | 45 | 45 | 49.3 | 107 | 78.7 | 73.6 | 46.3 | 1.7 | 0.1 | 6 | 5
2026-06-16 | 12AM | 2 | 45 | 44.8 | 48.5 | 92 | 77.5 | 73 | 39.3 | 1.5 | -0.2 | 6 | 5
2026-06-16 | 6AM | 2 | 45 | 44.8 | 48.6 | 94.5 | 78.6 | 73.7 | 41.5 | 1.6 | -0.4 | 6 | 5
2026-06-16 | 8AM | 2 | 45 | 45.1 | 49.5 | 109.4 | 81.5 | 77.6 | 51 | 1.8 | 1.5 | 6 | 5
2026-06-16 | 2PM | 2 | 45 | 45 | 50.2 | 129.4 | 80.5 | 74.1 | 56.1 | 2.1 | 0.6 | 6 | 5
2026-06-16 | 4PM | 2 | 45 | 45 | 49.7 | 116.9 | 80.5 |  | 52.2 | 1.9 | 0.5 | 6 | 5
2026-06-16 | 10PM | 2 | 45 | 45 | 49.2 | 104.5 | 81 | 75.8 | 48 | 1.7 | 0 | 6 | 5
2026-06-17 | 12AM | 2 | 45 | 45 | 49.2 | 104.5 | 82.1 | 77 | 48.2 | 1.7 | 0 | 6 | 5
2026-06-17 | 6AM | 2 | 45 | 45 | 49.6 | 114.4 | 84 | 79.6 | 54.8 | 1.8 | 1.2 | 6 | 5
2026-06-17 | 8AM | 2 | 45 | 45 | 49.9 | 121.9 | 82 | 76.2 | 54.2 | 1.9 | 0.1 | 6 | 5
2026-06-17 | 2PM | 2 | 45 | 45 | 49.7 | 116.9 | 80.2 | 74.8 | 51.7 | 1.9 | 0.5 | 6 | 5
2026-06-17 | 4PM | 2 | 45 | 45 | 49 | 99.5 | 78 | 73.3 | 42 | 1.6 |  | 6 | 5
2026-06-18 | 6AM | 2 | 47 | 47 | 52.6 | 139.3 | 82.8 | 76.7 | 54.6 | 2 | 0.7 | 6 | 5
2026-06-18 | 8AM | 2 | 45 | 45 | 50 | 124.4 | 80 | 74 | 58 | 2 | 0.7 | 6 | 5
2026-06-18 | 2PM | 2 | 45 | 45 | 50 | 124.4 | 80 | 74 | 60 | 2.2 | 0.8 | 6 | 5
2026-06-18 | 4PM | 2 | 45 | 45 | 49.6 | 114.4 | 81.6 | 77 | 52 | 1.9 | 1.1 | 6 | 5
2026-06-18 | 10PM | 2 | 45 | 45 | 49.9 | 121.9 | 83.7 | 79.8 | 47 | 1.6 | 0.9 | 6 | 5
2026-06-19 | 12AM | 2 | 45 | 44.8 | 48.4 | 89.6 | 78.5 | 73.5 | 44.7 | 1.7 | 0.2 | 6 | 5
2026-06-19 | 6AM | 2 | 45 | 44.7 | 48.5 | 94.5 | 78.1 | 73.3 | 43.3 | 1.5 | 0.3 | 6 | 5
2026-06-19 | 8AM | 2 | 47 | 47 | 53 | 149.2 | 81 | 75 | 50 | 1.7 | 0.4 | 6 | 5
2026-06-19 | 2PM | 2 | 47 | 47 | 52 | 124.4 | 80 | 75 | 52 | 1.9 | 0.5 | 6 | 5
2026-06-19 | 4PM | 2 | 47 | 52.4 | 54 | 39.8 | 80 | 74 | 56 | 2.1 | 0.9 | 6 | 5
2026-06-19 | 10PM | 2 | 47 | 51.3 | 51.3 |  | 77.7 | 72.6 | 44 | 1.7 | 0.2 | 6 | 5
2026-06-20 | 12AM | 2 | 47 | 46.9 | 50.8 | 97 | 81.2 | 76.3 | 43.5 | 1.6 | -0.4 | 6 | 5
2026-06-20 | 6AM | 2 | 47 | 47 | 51 | 99.5 | 78.5 | 75.2 | 43.5 | 1.5 | 1.4 | 6 | 5
2026-06-20 | 8AM | 2 | 45 | 45 | 49.3 | 107 | 80 | 74.9 | 47 | 1.7 | 0.1 | 6 | 5
2026-06-20 | 2PM | 2 | 45 | 45 | 50.2 | 129.4 | 80.2 | 74.3 | 56.1 | 2.1 | 0.6 | 6A | 5
2026-06-20 | 4PM | 2 | 45 | 45 | 50.2 | 129.4 | 80 | 74.2 | 56.3 | 2 | 0.7 | 6A | 5
2026-06-20 | 10PM | 2 | 45 | 45 | 49.4 | 109.4 | 78.6 | 73.6 | 47 | 1.7 | 0.3 | 6A | 5
2026-06-21 | 12AM | 2 | 45 | 44.9 | 49.5 | 114.4 | 84.1 | 78 | 52.5 | 1.9 | -0.3 | 6A | 5
2026-06-21 | 6AM | 2 | 45 | 45 | 49.4 | 109.4 | 84 | 79.7 | 52.8 | 1.7 | 1.1 | 6A | 5
2026-06-21 | 8AM | 2 | 45 | 45 | 49.6 | 114.4 | 85 | 81.2 | 51.3 | 1.7 | 0 | 6A | 5
2026-06-21 | 2PM | 2 | 45 | 44.9 | 50.6 | 141.8 | 81.8 | 75.4 | 62.5 | 2.2 | 0.6 | 6A | 5
2026-06-21 | 4PM | 2 | 45 | 45 | 50.7 | 141.8 | 82.4 | 76.4 | 64.2 | 2.2 | 0.7 | 6A | 5
2026-06-21 | 10PM | 2 | 45 | 45 | 51.7 | 166.7 | 85.4 | 78.1 | 75.5 | 2.5 | 0.8 | 6A | 5
2026-06-22 | 12AM | 2 | 45 | 45 | 51.3 | 156.7 | 83.5 | 76.7 | 68.6 | 2.4 | 0.7 | 6A | 5
2026-06-22 | 6AM | 2 | 45 | 45 | 50.2 | 129.4 | 84 | 78 | 58.4 | 2 | 0.1 | 6A | 5
2026-06-22 | 8AM | 2 | 45 | 45 | 50.6 | 139.3 | 81.4 | 75.2 | 58.6 | 2.1 | 0.4 | 6A | 5
2026-06-22 | 2PM | 2 | 45 | 45 | 51.3 | 156.7 | 85 | 77.9 | 72.3 | 2.5 | 0.7 | 6A | 5
2026-06-22 | 4PM | 2 | 45 | 45 | 50.7 | 141.8 | 83.4 | 76.9 | 64 | 2.2 | 0.7 | 6A | 5
2026-06-22 | 10PM | 2 | 45 | 45 | 49.2 | 104.5 | 81.3 | 77.1 | 47.8 | 1.6 | 1.1 | 6A | 5
2026-06-23 | 6AM | 2 | 45 | 43.7 | 47 | 82.1 | 81.6 | 78.2 | 42.3 | 1.7 | 0.9 | 6A | 5
2026-06-23 | 8AM | 2 | 45 | 45 | 50.2 | 129.4 | 81.4 | 75.3 | 57.4 | 2.1 | 0.4 | 6 | 5
2026-06-23 | 2PM | 2 | 45 | 45.1 | 50.8 | 141.8 | 80.9 | 74.4 | 62.6 | 2.3 | 0.8 | 6 | 5
2026-06-23 | 4PM | 2 | 45 | 45 | 50.2 | 129.4 | 80.4 | 74.6 | 56 | 2 | 0.7 | 6 | 5
2026-06-23 | 10PM | 2 | 45 | 45 | 49.3 | 107 | 83.7 | 79.6 | 50.3 | 1.8 | 1.1 | 6 | 5
2026-06-24 | 12AM | 2 | 45 | 45 | 49 | 99.5 | 82.8 | 77.9 | 52.3 | 2 | 1.3 | 6 | 5
2026-06-24 | 6AM | 2 | 45 | 45 | 49.6 | 114.4 | 80.8 | 75.2 | 49.6 | 1.8 | -0.2 | 6 | 5
2026-06-24 | 8AM | 2 | 45 | 44.9 | 49.1 | 104.5 | 80.7 | 75.5 | 46.3 | 1.7 | 0 | 6 | 5
2026-06-24 | 2PM | 2 | 45 | 45 | 50 | 124.4 | 81.6 | 75.7 | 55.2 | 2 | 0.3 | 6 | 5
2026-06-24 | 4PM | 2 | 45 | 45 | 49.5 | 111.9 | 83.7 | 79.6 | 51 | 1.8 | 1.3 | 6 | 5
2026-06-24 | 10PM | 2 | 45 | 45 | 49.7 | 116.9 | 81.6 | 75.9 | 52.7 | 1.9 | 0.1 | 6 | 5
2026-06-25 | 2PM | 1 | 45 | 45 | 51.4 | 159.2 | 81 | 76 | 54.4 | 1.5 | 2 | Both | Both | Started @ 12:11p - take offline when load can be carried by one chiller
2026-06-25 | 4PM | 1 | 45 | 45 | 52 | 174.1 | 81 | 76 | 61 | 1.8 | 2 | Both | Both
2026-06-25 | 10PM | 1 | 45 | 45 | 52 | 174.1 | 82.2 | 76 | 62 | 1.8 | 2.1 | Both | Both
2026-06-25 | 12AM | 2 | 45 | 45 | 49.8 | 119.4 | 80.4 | 74.8 | 51.9 | 1.9 | 0.4 | 6 | 5
2026-06-25 | 6AM | 2 | 45 | 45 | 50.4 | 134.3 | 80 | 74 | 56.7 | 2 | 0.6 | 6 | 5
2026-06-25 | 8AM | 2 | 45 | 45 | 52.3 | 181.6 | 86.5 | 78.6 | 82.8 | 2.8 | 1 | 6 | 5
2026-06-25 | 2PM | 2 | 45 | 45 | 51.3 | 156.7 | 81.9 | 76 | 50.3 | 1.7 | 0.4 | Both | Both
2026-06-25 | 4PM | 2 | 45 | 45 | 51 | 149.2 | 81 | 76 | 50 | 1.8 | 0.4 | 6 | 6
2026-06-25 | 10PM | 2 | 45 | 43 | 48.8 | 144.3 | 85 | 79.8 | 54.5 | 2.2 | 0.2 | 6A | 5A
2026-06-26 | 12AM | 2 | 45 | 45 | 52.3 | 181.6 | 81 | 73.4 | 51.1 | 1.7 | 0.4 | 6 | 5
2026-06-26 | 6AM | 2 | 45 | 45 | 51.8 | 169.1 | 85.9 | 79.7 | 53.8 | 1.6 | 1 | 6 | 5
2026-06-26 | 2PM | 2 | 45 | 45 | 52.8 | 194 | 89.7 | 77.7 | 72.2 | 2.5 | 0.7 | 6 | 5
2026-06-26 | 4PM | 2 | 45 | 45 | 51.7 | 166.7 | 81.8 | 75.7 | 60.7 | 2.1 | 0.7 | 6 | 5
2026-06-26 | 10PM | 2 | 45 | 45 | 51.5 | 161.7 | 80.6 | 74.8 | 57.3 | 2 | 0.7 | 6 | 5
2026-06-27 | 12AM | 2 | 45 | 45 | 51.5 | 161.7 | 82.1 | 75.9 | 56.3 | 1.8 | 0.3 | 6 | 5
2026-06-27 | 6AM | 2 | 45 | 45 | 51.1 | 151.7 | 82 | 76.1 | 55.1 | 1.9 | 0.1 | 6 | 5
2026-06-27 | 8AM | 2 | 45 | 45 | 52 | 174.1 | 80.9 | 74.8 | 60 | 2.1 | 0.7 | 6 | 5
2026-06-27 | 2PM | 2 | 45 | 45 | 51.5 | 161.7 | 81.6 | 75.7 | 59.4 | 2 | 0.7 | 6 | 5
2026-06-27 | 4PM | 2 | 45 | 45 | 51.7 | 166.7 | 82.5 | 76.5 | 62.1 | 2.1 | 0.7 | 6 | 5
2026-06-27 | 10PM | 2 | 45 | 45 | 52 | 174.1 | 85 | 78 | 70.8 | 2.4 | 0.7 | 6 | 5
2026-06-28 | 12AM | 2 | 45 | 45 | 51.7 | 166.7 | 81.7 | 75.6 | 61.1 | 1.9 | 0.8 | 6 | 5
2026-06-28 | 6AM | 2 | 45 | 45 | 50.9 | 146.8 | 79.1 | 74.7 | 51.4 | 1.7 | 1.3 | 6 | 5
2026-06-28 | 8AM | 2 | 45 | 45 | 52 | 174.1 | 81 | 74.8 | 60.1 | 2.1 | 0.7 | 6 | 5
2026-06-28 | 2PM | 2 | 45 | 45 | 53.4 | 208.9 | 89.6 | 81.9 | 85.1 |  | 0.9 | 6 | 5
2026-06-28 | 4PM | 2 | 45 | 45 | 54 | 223.9 | 85 | 76 | 92 |  | 2.2 | 6 | 5
2026-06-28 | 10PM | 2 | 45 | 45 | 55 | 248.8 | 88 | 84 | 95 | 2.6 | 3 | 6 | 5
2026-06-29 | 8AM | 1 | 45 | 45.1 | 51.4 | 156.7 | 82.1 | 77.2 | 53.9 | 1.5 | 1.9 | BOTH | BOTH | Online @ 9:15 AM (12AM/6AM offline)
2026-06-29 | 2PM | 1 | 44 | 44 | 51.9 | 196.5 | 93.6 | 89.9 | 71.3 | 1.8 | 1.9 | BOTH | BOTH
2026-06-29 | 4PM | 1 | 44 | 44 | 51.8 | 194 | 89.4 | 83.3 | 69.4 | 1.7 | 1.8 | BOTH | BOTH
2026-06-29 | 10PM | 1 | 44 | 44 | 51 | 174.1 | 87.5 | 81.5 | 62.1 | 1.8 | 1.8 | BOTH | BOTH
2026-06-29 | 12AM | 2 | 45 | 45 | 52.9 | 196.5 | 90.1 | 82 | 90.3 | 2.8 | 1 | 6 | 5
2026-06-29 | 6AM | 2 | 45 | 45 | 52.1 | 176.6 | 86.4 | 79.2 | 76.8 | 2.5 | 0.8 | 6 | 5
2026-06-29 | 8AM | 2 | 45 | 45 | 52.2 | 179.1 | 88.4 | 80.7 | 85.1 | 2.8 | 0.9 | 6 | 5
2026-06-29 | 2PM | 2 | 44 | 44 | 51.7 | 191.5 | 91.1 | 83.7 | 70.2 | 2.1 | 0.5 | BOTH | BOTH
2026-06-29 | 4PM | 2 | 44 | 44 | 51.6 | 189.1 | 90.8 | 83.2 | 69.1 | 2 | 0.6 | BOTH | BOTH
2026-06-29 | 10PM | 2 | 44 | 44.1 | 51.1 | 174.1 | 87.5 | 80.9 | 61 | 1.8 | 0.4 | BOTH | BOTH
2026-06-30 | 12AM | 1 | 45 | 45 | 51.8 | 169.1 | 85.7 | 80.4 | 60.2 | 1.5 | 1.8 | 6,6A | 5,5A
2026-06-30 | 6AM | 1 | 45 | 45 | 52.3 | 181.6 | 88.3 | 82.6 | 64.8 | 1.6 | 1.8 | 6,6A | 5,5A
2026-06-30 | 8AM | 1 | 45 | 45 | 52.2 | 179.1 | 89.4 | 83.8 | 66.7 | 1.6 | 1.9 | BOTH | BOTH | Set point to 44 @ 9:30 AM
2026-06-30 | 2PM | 1 | 44 | 44 | 52 | 199 | 92.5 | 86.1 | 74.9 | 1.8 | 1.9 | BOTH | BOTH
2026-06-30 | 4PM | 1 | 44 | 44 | 52.1 | 201.5 | 92.8 | 84.3 | 75.7 | 1.9 | 1.9 | BOTH | BOTH
2026-06-30 | 10PM | 1 | 44 | 44 | 51.9 | 196.5 | 92.3 | 85.9 | 73.8 | 1.8 | 1.9 | BOTH | BOTH
2026-06-30 | 12AM | 2 | 45 | 45 | 51.7 | 166.7 | 86.8 | 80.5 | 57.5 | 1.8 | 0.4 | 6,6A | 5,5A
2026-06-30 | 6AM | 2 | 45 | 45 | 52.1 | 176.6 | 89.4 | 82.7 | 63.1 | 1.9 | 0.5 | 6,6A | 5,5A
2026-06-30 | 8AM | 2 | 45 | 45 | 52 | 174.1 | 90.5 | 83.8 | 63.6 | 1.8 | 0.4 | BOTH | BOTH | Set point to 44 @ 9:32 AM
2026-06-30 | 2PM | 2 | 44 | 44 | 51.8 | 194 | 93.5 | 86.1 | 74.3 | 2.1 | 0.7 | BOTH | BOTH
2026-06-30 | 4PM | 2 | 44 | 44 | 52 | 199 | 93.9 | 85.6 | 75.6 | 2.2 | 0.7 | BOTH | BOTH
2026-06-30 | 10PM | 2 | 44 | 44 | 51.7 | 191.5 | 93.5 | 86.1 | 73.2 | 2.1 | 0.6 | BOTH | BOTH
2026-07-01 | 12AM | 1 | 44 | 44 | 51.4 | 184.1 | 90 | 84.1 | 69.4 | 1.7 | 1.9 | BOTH | BOTH
2026-07-01 | 6AM | 1 | 44 | 44 | 51.3 | 181.6 | 89.5 | 83.7 | 68.2 | 1.7 | 1.8 | BOTH | BOTH
2026-07-01 | 8AM | 1 | 45 | 45 | 52.5 | 186.6 | 90.6 | 84.7 | 69.4 | 1.7 | 1.9 | BOTH | BOTH
2026-07-01 | 2PM | 1 | 43 | 43 | 51.5 | 211.4 | 93.6 | 86.7 | 80.5 | 2 | 1.9 | BOTH | BOTH
2026-07-01 | 4PM | 1 | 43 | 43 | 51.3 | 206.5 | 92.4 | 85.7 | 76.9 | 1.9 | 1.9 | BOTH | BOTH
2026-07-01 | 10PM | 1 | 43 | 43 | 50.4 | 184.1 | 88.5 | 82.7 | 67.7 | 1.7 | 1.8 | BOTH | BOTH
2026-07-01 | 12AM | 2 | 44 | 44 | 51.3 | 181.6 | 91.1 | 84.2 | 67.1 | 1.9 | 0.5 | BOTH | BOTH
2026-07-01 | 6AM | 2 | 44 | 44 | 51.2 | 179.1 | 90.6 | 83.8 | 65.9 | 1.9 | 0.5 | BOTH | BOTH
2026-07-01 | 8AM | 2 | 45 | 45 | 52.3 | 181.6 | 91.8 | 84.9 | 67.3 | 1.9 | 0.6 | BOTH | BOTH
2026-07-01 | 2PM | 2 | 43 | 43 | 51.4 | 208.9 | 94.9 | 86.9 | 81.4 | 2.3 | 0.7 | BOTH | BOTH
2026-07-01 | 4PM | 2 | 43 | 43 | 51.2 | 204 | 93.8 | 85.9 | 78.6 | 2.3 | 0.8 | BOTH | BOTH
2026-07-01 | 10PM | 2 | 43 | 43 | 50.3 | 181.6 | 89.7 | 82.8 | 66.5 | 2 | 0.5 | BOTH | BOTH
2026-07-02 | 12AM | 1 | 43 | 43 | 50.1 | 176.6 | 87.5 | 81.9 | 65.7 | 1.7 | 1.8 | Both | Both
2026-07-02 | 6AM | 1 | 43 | 43 | 50.1 | 176.6 | 87.5 | 81.9 | 65.3 | 1.6 | 1.8 | Both | Both
2026-07-02 | 8AM | 1 | 43 | 43 | 51.2 | 204 | 92.4 | 85.8 | 77.4 | 1.9 | 1.9 | Both | Both
2026-07-02 | 2PM | 1 | 43 | 43 | 51 | 199 | 93.1 | 86.9 | 74 | 1.8 | 1.9 | Both | Both
2026-07-02 | 4PM | 1 | 43 | 43 | 51.4 | 208.9 | 91.1 | 84.7 | 73.8 | 1.9 | 2 | Both | Both
2026-07-02 | 10PM | 1 | 43 | 43 | 50.8 | 194 | 90.4 | 84.3 | 71.7 | 1.8 | 1.9 | Both | Both
2026-07-02 | 12AM | 2 | 43 | 43 | 50 | 174.1 | 88.6 | 82 | 63.4 | 1.9 | 0.4 | Both | Both
2026-07-02 | 6AM | 2 | 43 | 43 | 49.9 | 171.6 | 88.6 | 82.1 | 62.8 | 1.8 | 0.5 | Both | Both
2026-07-02 | 8AM | 2 | 43 | 43 | 51 | 199 | 93.5 | 85.8 | 76.6 | 2.2 | 0.7 | Both | Both
2026-07-02 | 2PM | 2 | 43 | 43 | 51.1 | 201.5 | 93.3 | 85.6 | 76.8 | 2.2 | 0.7 | Both | Both
2026-07-02 | 4PM | 2 | 43 | 43 | 50.4 | 184.1 | 92.2 | 84.7 | 74 | 2.1 | 0.9 | Both | Both
2026-07-02 | 10PM | 2 | 43 | 43 | 50.6 | 189.1 | 91.7 | 84.5 | 71.2 | 2 | 0.6 | Both | Both
2026-07-03 | 12AM | 1 | 43 | 43 | 50.6 | 189.1 | 89.9 | 83.9 | 70 | 1.8 | 1.8 | Both | Both
2026-07-03 | 6AM | 1 | 43 | 43 | 49.9 | 171.6 | 86.5 | 81.1 | 64 | 1.6 | 1.8 | Both | Both
2026-07-03 | 8AM | 1 | 43 | 43 | 50.1 | 176.6 | 87.1 | 81.5 | 65.5 | 1.4 | 1.8 | Both | Both | reading taken 9AM (8AM crossed out); cw_leaving 87.1 operator-confirmed
2026-07-03 | 2PM | 1 | 43 | 43 | 50.8 | 194 | 88.5 | 82.4 | 70.1 | 1.8 | 1.8 | Both | Both
2026-07-03 | 4PM | 1 | 43 | 43 | 51.2 | 204 | 91.4 | 85.1 | 75.4 | 1.9 | 2.2 | Both | Both
2026-07-03 | 10PM | 1 | 43 | 43 | 49.6 | 164.2 | 83.1 | 78.3 | 67.9 | 1.5 | 1.9 | Both | Both | cw_entering 78.3 confirmed by operator (barely legible)
2026-07-03 | 12AM | 2 | 43 | 43 | 50.4 | 184.1 | 91.1 | 84 | 68.9 | 2 | 0.6 | Both | Both
2026-07-03 | 6AM | 2 | 43 | 43 | 49.8 | 169.1 | 87.7 | 81.3 | 60.9 | 1.8 | 0.3 | Both | Both | chw_entering 49.8 operator-confirmed
2026-07-03 | 8AM | 2 | 43 | 43 | 50 | 174.1 | 88.1 | 81.5 | 62.6 | 1.9 | 0.4 | Both | Both | reading taken 9AM (8AM crossed out)
2026-07-03 | 2PM | 2 | 43 | 43 | 50.4 | 184.1 | 89.7 | 82.5 | 69.4 | 2 | 0.5 | Both | Both
2026-07-03 | 4PM | 2 | 43 | 43 | 51.1 | 201.5 | 92.8 | 85.2 | 76.3 | 2.2 | 0.8 | Both | Both
2026-07-03 | 10PM | 2 | 43 | 43 | 49.5 | 161.7 | 84.3 | 78.2 | 55.1 | 1.7 | 0.4 | Both | Both
2026-07-04 | 12AM | 1 | 43 | 43 | 49.2 | 154.2 | 81.4 | 76 | 55.1 | 1.5 | 2 | Both | Both
2026-07-04 | 6AM | 1 | 43 | 43 | 49.2 | 154.2 | 81.8 | 76.9 | 55.5 | 1.5 | 2 | Both | Both
2026-07-04 | 8AM | 1 | 43 | 43 | 49.6 | 164.2 | 83.8 | 78.7 | 59.1 | 1.5 | 1.8 | Both | Both
2026-07-04 | 2PM | 1 | 43 | 43 | 50.1 | 176.6 | 86.1 | 80.5 | 64 | 1.7 | 1.8 | Both | Both
2026-07-04 | 4PM | 1 | 43 | 43 | 50 | 174.1 | 87.7 | 81.9 | 66 | 1.7 | 1.9 | Both | Both | pumps Both per operator (boxes unmarked/checked on sheet)
2026-07-04 | 10PM | 1 | 43 | 43 | 49.8 | 169.1 | 84.9 | 79.6 | 66.4 | 1.6 | 1.8 | Both | Both | pumps Both per operator; chw_supply read 65 (sheet glyph resembles 45; Ch#2 evening also 65) - confirm
2026-07-04 | 12AM | 2 | 43 | 43 | 49.1 | 151.7 | 82.4 | 76.7 | 50.7 | 1.7 | 0.4 | Both | Both
2026-07-04 | 6AM | 2 | 43 | 43 | 49.1 | 151.7 | 82.8 | 77.1 | 51.3 | 1.7 | 0.4 | Both | Both
2026-07-04 | 8AM | 2 | 43 | 43 | 49.4 | 159.2 | 84.9 | 78.9 | 55.2 | 1.8 | 0.4 | Both | Both | reading taken 9AM (8AM crossed out)
2026-07-04 | 2PM | 2 | 43 | 43 | 49.9 | 171.6 | 87.1 | 80.5 | 61.3 | 1.9 | 0.4 | Both | Both
2026-07-04 | 4PM | 2 | 43 | 43 | 50 | 174.1 | 88 | 81.9 | 65 | 2 | 0.4 | Both | Both | pumps Both per operator (checkmarks on sheet = all pumps on)
2026-07-04 | 10PM | 2 | 43 | 43 | 49.7 | 166.7 | 86 | 79.7 | 58 | 1.8 | 0.4 | Both | Both | pumps Both per operator (checkmarks on sheet = all pumps on)
2026-07-05 | 12AM | 1 | 43 | 43 | 49.7 | 166.7 | 84.5 | 79.2 | 60.7 | 1.6 | 1.9 | Both | Both
2026-07-05 | 6AM | 1 | 43 | 43 | 49.3 | 156.7 | 82.4 | 77.5 | 56.7 | 1.5 | 1.9 | Both | Both
2026-07-05 | 8AM | 1 | 43 | 43 | 49.4 | 159.2 | 83 | 78.1 | 57.9 | 1.5 | 1.9 | Both | Both
2026-07-05 | 2PM | 1 | 45 | 45 | 51.1 | 151.7 | 84.1 | 79.4 | 56.2 | 1.4 | 1.8 | Both | Both | reading ~2:30p; SP raised 43->44 @2p, ->45 @2:10p
2026-07-05 | 4PM | 1 | 45 | 45 | 51.7 | 166.7 | 85.4 | 80.2 | 47.3 | 1.5 | 1.8 | Both | Both
2026-07-05 | 10PM | 1 | 45 | 45 | 51.3 | 156.7 | 83.1 | 78.3 | 57.1 | 1.4 | 1.9 | Both | Both
2026-07-05 | 12AM | 2 | 43 | 43 | 49.5 | 161.7 | 85.5 | 79.4 | 57 | 1.8 | 0.4 | Both | Both
2026-07-05 | 6AM | 2 | 43 | 43 | 49.2 | 154.2 | 83.4 | 77.6 | 52.4 | 1.6 | 0.4 | Both | Both
2026-07-05 | 8AM | 2 | 43 | 43 | 49.3 | 156.7 | 84.1 | 78.2 | 53.5 | 1.7 | 0.4 | Both | Both
2026-07-05 | 2PM | 2 | 45 | 44.5 | 51.1 | 164.2 | 85.6 | 79.6 | 55.2 | 1.7 | 0.4 | Both | Both | reading ~2:30p; SP raised 43->44 @2:10p, ->45 @2:30p
2026-07-05 | 4PM | 2 | 45 | 45 | 51.5 | 161.7 | 86.6 | 80.5 | 55.8 | 1.7 | 0.4 | Both | Both
2026-07-05 | 10PM | 2 | 45 | 45 | 51.1 | 151.7 | 84.2 | 78.4 | 51.2 | 1.6 | 0.3 | Both | Both
2026-07-06 | 12AM | 1 | 45 | 45 | 50.9 | 146.8 | 81 | 76.5 | 51.6 | 1.4 | 2 | Both | Both | Closed CW & CHW valves on Chiller #2
2026-07-06 | 6AM | 1 | 45 | 45 | 54.1 | 226.4 | 83 | 75.2 | 42.9 | 1.8 | 1.9 | 6 | 5A
2026-07-06 | 8AM | 1 | 45 | 45 | 52.4 | 184.1 | 83.2 | 76.5 | 73 | 2.3 | 2.4 | 6 | 5A
2026-07-06 | 2PM | 1 | 45 | 45 | 53.8 | 218.9 | 88.6 | 80.5 | 91.2 | 2.9 | 2.5 | 6 | 5A
2026-07-06 | 4PM | 1 | 45 | 48 | 53 | 124.4 | 87 | 80 | 91 | 2.8 | 2.4 | 6 | 5A | CHW leaving 48 > SP45 — #1 maxed, lead swapped to #2
2026-07-06 | 12AM | 2 | 45 | 45 | 50.8 | 144.3 | 82 | 76.6 | 44.6 | 1.5 | 0.4 | Both | Both | Off @ 2am; #6A CHW pump / #5 condenser pump
2026-07-06 | 10PM | 2 | 45 | 45 | 54 | 223.9 | 88.2 | 78 | 72.9 | 2.3 | 0.5 | 6 | 5A | Lead swapped back to #2; #1 off
2026-07-07 | 2PM | 1 | 45 | 45 | 51.7 | 166.7 | 85 | 79.8 | 59.2 | 1.5 | 1.9 | Both | Both | On @ 11AM
2026-07-07 | 4PM | 1 | 45 | 45 | 51.9 | 171.6 | 86.6 | 80.9 | 68 | 1.6 | 1.8 | Both | Both
2026-07-07 | 10PM | 1 | 45 | 45 | 53.2 | 204 | 88.8 | 82.3 | 76.4 | 1.7 | 1.9 | Both | Both | On @ 11AM day; 10PM cond lv/ent operator-confirmed 88.8/82.3
2026-07-07 | 12AM | 2 | 45 | 45 | 52.5 | 186.6 | 82.9 | 74.6 | 57.3 | 1.9 | 0.5 | 6 | 5A
2026-07-07 | 6AM | 2 | 45 | 45 | 51.9 | 171.6 | 82.2 | 74.4 | 51.4 | 1.7 | 0.2 | 6 | 5A
2026-07-07 | 8AM | 2 | 45 | 45 | 55.2 | 253.7 | 89.1 | 80.9 | 90 | 2.8 | 1.1 | 6 | 5A | read ~9:30
2026-07-07 | 2PM | 2 | 45 | 45 | 51.6 | 164.2 | 87 | 80.1 | 62 | 1.9 | 0.4 | Both | Both
2026-07-07 | 4PM | 2 | 45 | 45 | 51.8 | 169.1 | 87.8 | 81.1 | 61 | 1.9 | 0.4 | Both | Both
2026-07-07 | 10PM | 2 | 45 | 45 | 53.1 | 201.5 | 90.1 | 82.5 | 71 | 2.1 | 0.6 | Both | Both
2026-07-08 | 12AM | 1 | 45 | 45 | 52.8 | 194 | 87 | 80.9 | 44.4 | 1.1 | 1.9 | Both | Both
2026-07-08 | 6AM | 1 | 45 | 45 | 52.3 | 181.6 | 85.1 | 79.4 | 62.3 | 1.6 | 1.9 | Both | Both
2026-07-08 | 8AM | 1 | 45 | 45 | 52.8 | 194 | 87.2 | 81.1 | 66.4 | 1.7 | 1.9 | Both | Both
2026-07-08 | 2PM | 1 | 45 | 45 | 51.2 | 154.2 | 81.1 | 76.1 | 54.2 | 1.5 | 2 | Both | Both
2026-07-08 | 4PM | 1 | 45 | 45 | 51.2 | 154.2 | 80.9 | 76 | 53.6 | 1.5 | 2.1 | Both | Both | Chiller #1 taken offline at 8PM — no 10PM reading; #2 carried the load solo after.
2026-07-08 | 12AM | 2 | 45 | 45 | 52.6 | 189.1 | 88.5 | 81 | 65.9 | 2 | 0.4 | Both | Both
2026-07-08 | 6AM | 2 | 45 | 45 | 52.2 | 179.1 | 86.3 | 79.6 | 60.7 | 1.9 | 0.5 | Both | Both
2026-07-08 | 8AM | 2 | 45 | 45 | 52.7 | 191.5 | 88.5 | 81.2 | 47 | 2 | 0.5 | Both | Both
2026-07-08 | 2PM | 2 | 45 | 45 | 51.1 | 151.7 | 82.3 | 76.3 | 51.9 | 1.7 | 0.4 | Both | Both
2026-07-08 | 4PM | 2 | 45 | 45 | 51 | 149.2 | 82.1 | 76.2 | 50.6 | 1.6 | 0.5 | Both | Both
2026-07-08 | 10PM | 2 | 45 | 45 | 51.3 | 156.7 | 83.1 | 76 | 70.2 | 2.3 | 0.8 | Both | Both
2026-07-09 | 8AM | 1 | 45 | 45 | 52.8 | 194 | 86.5 | 80.4 | 65.5 | 1.7 | 1.9 | Both | Both | Started 6:20AM
2026-07-09 | 2PM | 1 | 45 | 45 | 52 | 174.1 | 86.5 | 80.8 | 64 | 1.6 | 1.8 | Both | Both
2026-07-09 | 4PM | 1 | 45 | 45 | 51.9 | 171.6 | 85.9 | 80.3 | 61.9 | 1.6 | 1.8 | Both | Both
2026-07-09 | 10PM | 1 | 45 | 45 | 52.6 | 189.1 | 88.3 | 80.4 | 64.1 | 1.6 | 1.9 | Both | Both
2026-07-09 | 12AM | 2 | 45 | 44.9 | 52.8 | 196.5 | 84.7 | 76.1 | 93 | 7.4 | 2.3 | 6 | 5
2026-07-09 | 6AM | 2 | 45 | 45.1 | 54.3 | 228.8 | 88.1 | 79.5 | 99.8 | 8.3 | 3 | 6 | 5 | #2 solo overnight; #1 started 6:20AM
2026-07-09 | 8AM | 2 | 45 | 45 | 52.5 | 186.6 | 87.6 | 80.5 | 64.4 | 1.9 | 0.5 | Both | Both
2026-07-09 | 2PM | 2 | 45 | 45 | 51.8 | 169.1 | 87.7 | 80.9 | 62.5 | 1.9 | 0.5 | Both | Both
2026-07-09 | 4PM | 2 | 45 | 45 | 51.9 | 171.6 | 87.2 | 80.6 | 61.2 | 1.9 | 0.4 | Both | Both
2026-07-09 | 10PM | 2 | 45 | 45 | 52.6 | 189.1 | 87.6 | 80.5 | 64.7 | 1.9 | 0.5 | Both | Both
2026-07-10 | 12AM | 1 | 45 | 45 | 52.4 | 184.1 | 85.6 | 79.8 | 62.2 | 1.6 | 1.9 | Both | Both
2026-07-10 | 6AM | 1 | 45 | 45 | 51.7 | 166.7 | 82.3 | 77.3 | 55.7 | 1.5 | 1.9 | Both | Both
2026-07-10 | 8AM | 1 | 45 | 45 | 52.4 | 184.1 | 82.5 | 77.4 | 56.2 | 1.5 | 2 | 6A | Both | 8AM: dropped to one CHW pump
2026-07-10 | 2PM | 1 | 44 | 44 | 52.2 | 204 | 86.2 | 80.5 | 64.1 | 1.6 | 1.8 | 6A | Both | SP lowered 45→44 at 10:41 AM (leaving temp follows)
2026-07-10 | 4PM | 1 | 44 | 44 | 52.3 | 206.5 | 87.9 | 82 | 66.3 | 1.6 | 1.8 | 6A | Both
2026-07-10 | 10PM | 1 | 44 | 44 | 52.5 | 211.4 | 87.8 | 80.7 | 64.5 | 1.6 | 1.8 | 6A | Both
2026-07-10 | 12AM | 2 | 45 | 45 | 52.3 | 181.6 | 86.8 | 79.9 | 61.7 | 1.9 | 0.4 | Both | Both
2026-07-10 | 6AM | 2 | 45 | 45 | 51.6 | 164.2 | 83.6 | 77.4 | 53.5 | 1.7 | 0.4 | Both | Both
2026-07-10 | 8AM | 2 | 45 | 45 | 52.3 | 181.6 | 83.8 | 77.1 | 53.6 | 1.7 | 0.5 | 6A | Both
2026-07-10 | 2PM | 2 | 44 | 44 | 52 | 199 | 87.6 | 80.6 | 64.5 | 1.9 | 0.5 | 6A | Both | SP lowered 45→44 at 10:41 AM (leaving temp follows)
2026-07-10 | 4PM | 2 | 44 | 44 | 52.2 | 204 | 89.4 | 82.2 | 68.2 | 2 | 0.6 | 6A | Both
2026-07-10 | 10PM | 2 | 44 | 44 | 52.4 | 208.9 | 88.2 | 80.9 | 67.2 | 2 | 0.5 | 6A | Both
2026-07-11 | 12AM | 1 | 44.3 | 44.3 | 52.1 | 194 | 83 | 77.8 | 58.1 | 1.5 | 1.9 | 6A | Both | ACTIVE SETPOINT ON, CHW RESET OFF — setpoint floats per slot
2026-07-11 | 6AM | 1 | 47.2 | 47.2 | 52.1 | 121.9 | 84.9 | 81.5 | 48.9 | 1 | 1.6 | 6A | Both
2026-07-11 | 8AM | 1 | 44 | 44 | 50.9 | 171.6 | 82.7 | 77.9 | 55.1 | 1.4 | 1.8 | 6A | Both
2026-07-11 | 2PM | 1 | 45 | 45 | 50.8 | 144.3 | 84.9 | 80.8 | 53.9 | 1.2 | 1.7 | 6A | Both
2026-07-11 | 4PM | 1 | 45 | 45 | 51.4 | 159.2 | 80.7 | 76.2 | 50 | 1.3 | 2 | 6A | Both
2026-07-11 | 10PM | 1 | 48 | 48 | 51.1 | 77.1 | 85.4 | 81.2 | 53.7 | 2.1 | 1.7 | 6A | Both
2026-07-11 | 12AM | 2 | 44.7 | 44.6 | 51.9 | 181.6 | 84.2 | 78 | 55 | 1.7 | 0.4 | 6A | Both | ACTIVE SETPOINT ON, CHW RESET OFF — setpoint floats per slot
2026-07-11 | 6AM | 2 | 45.5 | 45.4 | 51.9 | 161.7 | 87.2 | 81.7 | 52.5 | 1.5 | 0.3 | 6A | Both
2026-07-11 | 8AM | 2 | 44 | 43.6 | 50.7 | 176.6 | 85.9 | 79.2 | 55.1 | 1.6 | 0 | 6A | Both
2026-07-11 | 2PM | 2 | 45 | 44.9 | 50.7 | 144.3 | 85.7 | 80.6 | 50.2 | 1.6 | 0.6 | 6A | Both
2026-07-11 | 4PM | 2 | 45 | 45 | 51.3 | 156.7 | 80.7 | 76.3 | 49.8 | 1.9 | 0.5 | 6A | Both
2026-07-11 | 10PM | 2 | 45 | 45 | 50.9 | 146.8 | 85.8 | 80.5 | 50.5 | 1.1 | 0.4 | 6A | Both
2026-07-12 | 8AM | 1 | 45 | 45.1 | 53.4 | 206.5 | 83.2 | 77.7 | 58.4 | 1.5 | 2 | Both | 5A,5 | Started 9:50am; reading taken 10AM
2026-07-12 | 2PM | 1 | 45 | 45 | 50.2 | 129.4 | 80 | 75.5 | 49.4 | 1.3 | 1.9 | Both | 5A,5
2026-07-12 | 12AM | 2 | 45 | 45 | 50.5 | 136.8 | 80.2 | 74.2 | 58.5 | 2.1 | 0.7 | 6A | 5A | Adj setpoint 45
2026-07-12 | 6AM | 2 | 45 | 45 | 51.6 | 164.2 | 82.4 | 75.5 | 69.7 | 2.4 | 0.9 | 6A | 5A
2026-07-12 | 8AM | 2 | 45 | 45 | 53 | 199 | 87.8 | 79.7 | 87.8 | 2.9 | 1 | 6A | 5A
2026-07-12 | 2PM | 2 | 45 | 44.1 | 49.9 | 144.3 | 83.1 | 76.7 | 47.6 | 1.5 | 0 | Both | 5A,5
2026-07-12 | 4PM | 2 | 45 | 45 | 53 | 199 | 88.5 | 79.7 | 86.9 | 2.8 | 0.9 | 6A | 5A,5
2026-07-12 | 10PM | 2 | 45 | 45 | 52.4 | 184.1 | 85.5 | 77.2 | 76 | 2.6 | 0.7 | 6A | 5
2026-07-13 | 6AM | 1 | 45 | 45 | 49.9 | 121.9 | 85 | 81.1 | 52.6 | 1.2 | 1.6 | Both | Both
2026-07-13 | 8AM | 1 | 45 | 45 | 54.5 | 236.3 | 86.3 | 78.4 | 81.7 | 2.6 | 2.3 | 6A | 5 | reading taken 9AM
2026-07-13 | 2PM | 1 | 45 | 45.1 | 55.3 | 253.7 | 86.5 | 76.9 | 99 | 2.9 | 3 | 6A | 5
2026-07-13 | 4PM | 1 | 45 | 45 | 51.7 | 166.7 | 84.4 | 76.5 | 58.9 | 1.4 | 1.7 | Both | Both
2026-07-13 | 10PM | 1 | 45 | 45 | 51.6 | 164.2 | 85.2 | 80 | 52.8 | 1.3 | 1.7 | Both | Both
2026-07-13 | 12AM | 2 | 45 | 45 | 51.5 | 161.7 | 82.3 | 75.9 | 44 | 2.2 | 0.8 | 6A | 5 | Active setpoint on; off ~8am, cycled back on 2:30pm (2PM reading not taken)
2026-07-13 | 6AM | 2 | 43 | 43 | 49.8 | 169.1 | 89.5 | 81.2 | 59.5 | 1.8 | 0.2 | Both | Both
2026-07-13 | 8AM | 2 | 45 | 45 | 51.6 | 164.2 | 81.8 | 76.2 | 59.4 | 1.2 | 2 | Both | Both
2026-07-13 | 4PM | 2 | 45 | 45 | 51.6 | 164.2 | 87.8 | 82.7 | 59.3 | 1.4 | 2 | Both | Both
2026-07-13 | 10PM | 2 | 45 | 45 | 51.6 | 164.2 | 87.8 | 80.2 | 58.8 | 1.8 | 3 | Both | Both

## Daily
Date | Plant Peak Tons | Plant Avg Tons | C1 Peak RLA % | C2 Peak RLA % | Evap ΔT °F | Cond ΔT °F | MA Enthalpy | OA Enthalpy
2026-06-09 | 443 | 347 | 78.4 | 88 | 8.4 | 8
2026-06-10 | 465 | 411 | 83 | 90 | 8.3 | 7.4
2026-06-11 | 393 | 370 | 67.9 | 70.1 | 7.4 | 6.3
2026-06-12 | 351 | 249 | 63.6 | 77 | 6.7 | 6.1
2026-06-13 | 206 | 175 |  | 86.2 | 7 | 6.7
2026-06-14 | 216 | 172 |  | 92.3 | 6.9 | 6
2026-06-15 | 112 | 95 |  | 52.3 | 3.8 | 4.6
2026-06-16 | 129 | 108 |  | 56.1 | 4.3 | 5
2026-06-17 | 122 | 111 |  | 54.8 | 4.5 | 5.1
2026-06-18 | 139 | 125 |  | 60 | 5 | 5.3
2026-06-19 | 149 | 100 |  | 56 | 4 | 5.3
2026-06-20 | 129 | 112 |  | 56.3 | 4.5 | 5
2026-06-21 | 167 | 131 |  | 75.5 | 5.3 | 5.6
2026-06-22 | 157 | 138 |  | 72.3 | 5.6 | 6.1
2026-06-23 | 142 | 118 |  | 62.6 | 4.7 | 5.2
2026-06-24 | 124 | 112 |  | 55.2 | 4.5 | 5.2
2026-06-25 | 323 | 232 | 62 | 82.8 | 6.2 | 5.8
2026-06-26 | 194 | 175 |  | 72.2 | 7 | 7.5
2026-06-27 | 174 | 165 |  | 70.8 | 6.6 | 6.2
2026-06-28 | 249 | 195 |  | 95 | 7.8 | 6.2
2026-06-29 | 388 | 305 | 71.3 | 90.3 | 7.3 | 6.5
2026-06-30 | 400 | 371 | 75.7 | 75.6 | 7.5 | 6.7
2026-07-01 | 420 | 382 | 80.5 | 81.4 | 7.7 | 6.7
2026-07-02 | 403 | 380 | 77.4 | 76.8 | 7.6 | 6.6
2026-07-03 | 406 | 362 | 75.4 | 76.3 | 7.3 | 6.3
2026-07-04 | 348 | 328 | 66.4 | 65 | 6.6 | 5.7
2026-07-05 | 328 | 318 | 60.7 | 57 | 6.4 | 5.5
2026-07-06 | 291 | 211 | 91.2 | 72.9 | 7.3 | 7.1
2026-07-07 | 406 | 282 | 76.4 | 90 | 7.5 | 7
2026-07-08 | 386 | 316 | 66.4 | 70.2 | 6.9 | 6.2
2026-07-09 | 381 | 312 | 65.5 | 99.8 | 7.5 | 7
2026-07-10 | 420 | 383 | 66.3 | 68.2 | 7.7 | 6.3
2026-07-11 | 376 | 306 | 58.1 | 55.1 | 6.1 | 5
2026-07-12 | 406 | 227 | 58.4 | 87.8 | 6.8 | 6.8
2026-07-13 | 400 | 294 | 99 | 59.5 | 7.1 | 6.7