## Overview
Building Overview
Data export · 2026-06-09 → 2026-07-17 · 39 days · generated 2026-07-18 02:06
PEAK PLANT LOAD | TOTAL TON-HOURS | TOTAL kWh | AVG kW/TON
465.5 | 202459 | 111855 | 0.58
PEAK ENTHALPY | PEAK OA TEMP | DAYS COOLING | TOTAL WATER
44.7 | 99.1 | 35 | 375860
Tabs → 📈 Load · Weather · Water are view-only charts; Daily / Chiller / BMS hold the data.

## Chiller (per-slot)
Date | Slot | Chiller | Set Pt | CHW Lv | CHW Ent | Tons | Cond Lv | Cond Ent | RLA % | CHW Pump | Cond Pump | Notes
2026-06-09 | 6AM | 1 | 45 | 49.7 | 54.5 | 119.5 | 83.4 | 79.8 | 45.5 | ALL | ALL | Started #1 chiller @ 6:15pm
2026-06-09 | 8AM | 1 | 45 | 45 | 53 | 199.1 | 87 | 81 | 65 | All | All
2026-06-09 | 4PM | 1 | 45 | 45 | 54 | 224 | 93.6 | 86.7 | 78.4 | 5 | 6
2026-06-09 | 10PM | 1 | 45 | 45 | 53.9 | 221.5 | 91.5 | 84.5 | 74.6 | 5 | 6
2026-06-09 | 12AM | 2 | 45 | 45 | 53 | 199.1 | 88.2 | 78.8 | 67.8 | 6 | 5
2026-06-09 | 6AM | 2 | 45 | 45.1 | 56.6 | 286.3 | 91.2 | 77.8 | 69.8 | 6 | 5
2026-06-09 | 8AM | 2 | 45 | 45 | 52 | 174.2 | 89 | 82 | 73 | 6 | 5
2026-06-09 | 2PM | 2 | 45 | 45 | 53.8 | 219 | 95 | 86.8 | 88 | 6 | 5
2026-06-09 | 4PM | 2 | 45 | 45 | 53.8 | 219 | 95 | 86 | 88 | 6 | 5
2026-06-09 | 10PM | 2 | 45 | 45 | 53.8 | 219 | 95 | 86 | 86 | 6 | 5
2026-06-10 | 12AM | 1 | 45 | 45 | 52.3 | 181.7 | 85 | 79.6 | 59.8 | Both | Both
2026-06-10 | 6AM | 1 | 45 | 45 | 52.8 | 194.2 | 87.4 | 81.6 | 64.6 | Both | Both
2026-06-10 | 8AM | 1 | 45 | 45.1 | 53.3 | 204.1 | 89.3 | 82.9 | 70.5 | Both | Both
2026-06-10 | 2PM | 1 | 45 | 45 | 54.2 | 229 | 93.5 | 86.2 | 80.4 | Both | Both
2026-06-10 | 4PM | 1 | 45 | 45 | 54.4 | 234 | 95.3 | 87.8 | 83 | Both | Both
2026-06-10 | 10PM | 1 | 45 | 45 | 53.5 | 211.6 | 89.7 | 83.1 |  | Both | Both
2026-06-10 | 12AM | 2 | 45 | 45 | 51.1 | 151.8 | 85.7 | 77.8 | 61 | Both | Both
2026-06-10 | 6AM | 2 | 45 | 45 | 52.7 | 191.7 | 89.4 | 81.7 | 70.7 | Both | Both
2026-06-10 | 8AM | 2 | 45 | 45 | 53.2 | 204.1 | 90.8 | 83 | 73.8 | Both | Both
2026-06-10 | 2PM | 2 | 45 | 45 | 54.1 | 226.5 | 95.6 | 86.5 | 86.5 | Both | Both
2026-06-10 | 4PM | 2 | 45 | 45 | 54.3 | 231.5 | 97 | 88 | 90 | Both | Both
2026-06-10 | 10PM | 2 | 45 | 45 | 53.4 | 209.1 | 91.6 | 83.2 | 75.6 | Both | Both
2026-06-11 | 12AM | 1 | 45 | 45 | 52.5 | 186.7 | 85.4 | 79.6 | 61.8 | 6,6A | 5,5A
2026-06-11 | 6AM | 1 | 45 | 45 | 52 | 174.2 | 83.1 | 77.8 | 57.4 | 6,6A | 5,5A
2026-06-11 | 8AM | 1 | 45 | 44.9 | 52.4 | 186.7 | 85.4 | 79.8 | 62.6 | Both | Both
2026-06-11 | 2PM | 1 | 45 | 45.1 | 53 | 196.6 | 88 | 81.7 | 67.9 | Both | Both
2026-06-11 | 4PM | 1 | 45 | 45 | 52.9 | 196.6 | 88.1 | 82 | 67.1 | Both | Both
2026-06-11 | 10PM | 1 | 45 | 45 | 52.2 | 179.2 | 86.9 | 81 | 64.2 | Both | Both
2026-06-11 | 12AM | 2 | 45 | 45 | 52.4 | 184.2 | 87.3 | 80.1 | 63.8 | 6,6A | 5,5A
2026-06-11 | 6AM | 2 | 45 | 45 | 51.8 | 169.3 | 84.3 | 77.8 | 56.7 | 6,6A | 5,5A
2026-06-11 | 8AM | 2 | 45 | 45 | 52.3 | 181.7 | 86.8 | 79.9 | 62.3 | Both | Both
2026-06-11 | 2PM | 2 | 45 | 45 | 52.9 | 196.6 | 89.6 | 81.9 | 70.1 | Both | Both
2026-06-11 | 4PM | 2 | 45 | 45 | 52.7 | 191.7 | 87.7 | 82.2 | 67.2 | Both | Both
2026-06-11 | 10PM | 2 | 45 | 45 | 52.1 | 176.7 | 88.2 | 81 | 65.1 | Both | Both
2026-06-12 | 12AM | 1 | 45 | 45 | 52.2 | 179.2 | 86.7 | 80.8 | 63.6 | 6,6A | 5,5A | OFF @ 9:50am
2026-06-12 | 6AM | 1 | 45 | 45 | 51.8 | 169.3 | 82.5 | 77.3 | 58.1 | 6,6A | 5,5A
2026-06-12 | 8AM | 1 | 45 | 45 | 50.8 | 144.4 | 82.9 | 78.5 | 53.1 | Both | Both
2026-06-12 | 12AM | 2 | 45 | 45 | 51.9 | 171.8 | 87.9 | 80.9 | 63.7 | 6,6A | 5,5A | Cycled @ 8:41a
2026-06-12 | 6AM | 2 | 45 | 45 | 51.7 | 166.8 | 84 | 77.6 | 54.9 | 6,6A | 5,5A
2026-06-12 | 8AM | 2 | 45 | 44.9 | 50.6 | 141.9 | 83.1 | 78.1 | 48.6 | Both | Both
2026-06-12 | 2PM | 2 | 45 | 45 | 52.4 | 184.2 | 85.2 | 77.8 | 74 | 6A | 5
2026-06-12 | 4PM | 2 | 45 | 45 | 52.7 | 191.7 | 85.6 | 78.1 | 77 | Both | Both
2026-06-12 | 10PM | 2 | 45 | 45 | 50.9 | 146.9 | 79.5 | 73.7 | 54 | 6,6 | 5,5
2026-06-13 | 12AM | 2 | 45 | 45 | 50.9 | 146.9 | 78.4 | 73.7 | 54.7 | 6A | 5
2026-06-13 | 6AM | 2 | 45 | 45 | 50.8 | 144.4 | 79.1 | 73.5 | 52.6 | 6,6A | 5
2026-06-13 | 8AM | 2 | 45 | 45 | 53.3 | 206.6 | 88.6 | 80.5 | 86.2 | 6A | 5
2026-06-13 | 2PM | 2 | 45 | 45 | 52.6 | 189.2 | 87.6 | 80.1 | 79.1 | 6A | 5
2026-06-13 | 4PM | 2 | 45 | 45 | 52.4 | 184.2 | 88 | 80.6 | 77 | 6A | 5
2026-06-13 | 10PM | 2 | 45 | 45 | 52.3 | 181.7 | 87.1 | 79.9 | 75 | 6A | 5
2026-06-14 | 12AM | 2 | 45 | 45 | 51 | 149.3 | 82.2 | 76.4 | 58.2 | 6A | 5
2026-06-14 | 6AM | 2 | 45 | 45 | 53.5 | 211.6 | 84.8 | 81.7 | 88.3 | 6A | 5
2026-06-14 | 8AM | 2 | 45 | 45 | 53.7 | 216.6 | 91 | 82.6 | 92.3 | 6A | 5
2026-06-14 | 2PM | 2 | 45 | 45 | 51.7 | 166.8 | 83.5 | 76.5 | 69.4 | 6A | 5
2026-06-14 | 4PM | 2 | 45 | 45 | 51.4 | 159.3 | 82.2 |  | 66 | 6A | 5
2026-06-14 | 10PM | 2 | 45 | 45 | 50.3 | 131.9 | 81.7 | 75.9 | 55 | 6A | 5
2026-06-15 | 12AM | 2 | 45 | 51.8 | 54.8 | 74.7 | 76.1 | 73.7 | 37.4 | 6A | 5
2026-06-15 | 6AM | 2 | 45 | 52.1 | 55 | 72.2 | 75.8 | 73.2 | 30.5 | 6A | 5
2026-06-15 | 8AM | 2 | 45 | 44.7 | 48.7 | 99.6 | 80.3 | 75.3 | 44.8 | 6 | 5
2026-06-15 | 2PM | 2 | 45 | 45 | 49.3 | 107 | 83.8 | 79.7 | 51.5 | 6 | 5
2026-06-15 | 4PM | 2 | 45 | 45 | 49.5 | 112 | 83.6 | 75.2 | 52.3 | 6 | 5
2026-06-15 | 10PM | 2 | 45 | 45 | 49.3 | 107 | 78.7 | 73.6 | 46.3 | 6 | 5
2026-06-16 | 12AM | 2 | 45 | 44.8 | 48.5 | 92.1 | 77.5 | 73 | 39.3 | 6 | 5
2026-06-16 | 6AM | 2 | 45 | 44.8 | 48.6 | 94.6 | 78.6 | 73.7 | 41.5 | 6 | 5
2026-06-16 | 8AM | 2 | 45 | 45.1 | 49.5 | 109.5 | 81.5 | 77.6 | 51 | 6 | 5
2026-06-16 | 2PM | 2 | 45 | 45 | 50.2 | 129.4 | 80.5 | 74.1 | 56.1 | 6 | 5
2026-06-16 | 4PM | 2 | 45 | 45 | 49.7 | 117 | 80.5 |  | 52.2 | 6 | 5
2026-06-16 | 10PM | 2 | 45 | 45 | 49.2 | 104.5 | 81 | 75.8 | 48 | 6 | 5
2026-06-17 | 12AM | 2 | 45 | 45 | 49.2 | 104.5 | 82.1 | 77 | 48.2 | 6 | 5
2026-06-17 | 6AM | 2 | 45 | 45 | 49.6 | 114.5 | 84 | 79.6 | 54.8 | 6 | 5
2026-06-17 | 8AM | 2 | 45 | 45 | 49.9 | 122 | 82 | 76.2 | 54.2 | 6 | 5
2026-06-17 | 2PM | 2 | 45 | 45 | 49.7 | 117 | 80.2 | 74.8 | 51.7 | 6 | 5
2026-06-17 | 4PM | 2 | 45 | 45 | 49 | 99.6 | 78 | 73.3 | 42 | 6 | 5
2026-06-18 | 6AM | 2 | 47 | 47 | 52.6 | 139.4 | 82.8 | 76.7 | 54.6 | 6 | 5
2026-06-18 | 8AM | 2 | 45 | 45 | 50 | 124.5 | 80 | 74 | 58 | 6 | 5
2026-06-18 | 2PM | 2 | 45 | 45 | 50 | 124.5 | 80 | 74 | 60 | 6 | 5
2026-06-18 | 4PM | 2 | 45 | 45 | 49.6 | 114.5 | 81.6 | 77 | 52 | 6 | 5
2026-06-18 | 10PM | 2 | 45 | 45 | 49.9 | 122 | 83.7 | 79.8 | 47 | 6 | 5
2026-06-19 | 12AM | 2 | 45 | 44.8 | 48.4 | 89.6 | 78.5 | 73.5 | 44.7 | 6 | 5
2026-06-19 | 6AM | 2 | 45 | 44.7 | 48.5 | 94.6 | 78.1 | 73.3 | 43.3 | 6 | 5
2026-06-19 | 8AM | 2 | 47 | 47 | 53 | 149.3 | 81 | 75 | 50 | 6 | 5
2026-06-19 | 2PM | 2 | 47 | 47 | 52 | 124.5 | 80 | 75 | 52 | 6 | 5
2026-06-19 | 4PM | 2 | 47 | 52.4 | 54 | 39.8 | 80 | 74 | 56 | 6 | 5
2026-06-19 | 10PM | 2 | 47 | 51.3 | 51.3 | 0 | 77.7 | 72.6 | 44 | 6 | 5
2026-06-20 | 12AM | 2 | 47 | 46.9 | 50.8 | 97.1 | 81.2 | 76.3 | 43.5 | 6 | 5
2026-06-20 | 6AM | 2 | 47 | 47 | 51 | 99.6 | 78.5 | 75.2 | 43.5 | 6 | 5
2026-06-20 | 8AM | 2 | 45 | 45 | 49.3 | 107 | 80 | 74.9 | 47 | 6 | 5
2026-06-20 | 2PM | 2 | 45 | 45 | 50.2 | 129.4 | 80.2 | 74.3 | 56.1 | 6A | 5
2026-06-20 | 4PM | 2 | 45 | 45 | 50.2 | 129.4 | 80 | 74.2 | 56.3 | 6A | 5
2026-06-20 | 10PM | 2 | 45 | 45 | 49.4 | 109.5 | 78.6 | 73.6 | 47 | 6A | 5
2026-06-21 | 12AM | 2 | 45 | 44.9 | 49.5 | 114.5 | 84.1 | 78 | 52.5 | 6A | 5
2026-06-21 | 6AM | 2 | 45 | 45 | 49.4 | 109.5 | 84 | 79.7 | 52.8 | 6A | 5
2026-06-21 | 8AM | 2 | 45 | 45 | 49.6 | 114.5 | 85 | 81.2 | 51.3 | 6A | 5
2026-06-21 | 2PM | 2 | 45 | 44.9 | 50.6 | 141.9 | 81.8 | 75.4 | 62.5 | 6A | 5
2026-06-21 | 4PM | 2 | 45 | 45 | 50.7 | 141.9 | 82.4 | 76.4 | 64.2 | 6A | 5
2026-06-21 | 10PM | 2 | 45 | 45 | 51.7 | 166.8 | 85.4 | 78.1 | 75.5 | 6A | 5
2026-06-22 | 12AM | 2 | 45 | 45 | 51.3 | 156.8 | 83.5 | 76.7 | 68.6 | 6A | 5
2026-06-22 | 6AM | 2 | 45 | 45 | 50.2 | 129.4 | 84 | 78 | 58.4 | 6A | 5
2026-06-22 | 8AM | 2 | 45 | 45 | 50.6 | 139.4 | 81.4 | 75.2 | 58.6 | 6A | 5
2026-06-22 | 2PM | 2 | 45 | 45 | 51.3 | 156.8 | 85 | 77.9 | 72.3 | 6A | 5
2026-06-22 | 4PM | 2 | 45 | 45 | 50.7 | 141.9 | 83.4 | 76.9 | 64 | 6A | 5
2026-06-22 | 10PM | 2 | 45 | 45 | 49.2 | 104.5 | 81.3 | 77.1 | 47.8 | 6A | 5
2026-06-23 | 6AM | 2 | 45 | 43.7 | 47 | 82.1 | 81.6 | 78.2 | 42.3 | 6A | 5
2026-06-23 | 8AM | 2 | 45 | 45 | 50.2 | 129.4 | 81.4 | 75.3 | 57.4 | 6 | 5
2026-06-23 | 2PM | 2 | 45 | 45.1 | 50.8 | 141.9 | 80.9 | 74.4 | 62.6 | 6 | 5
2026-06-23 | 4PM | 2 | 45 | 45 | 50.2 | 129.4 | 80.4 | 74.6 | 56 | 6 | 5
2026-06-23 | 10PM | 2 | 45 | 45 | 49.3 | 107 | 83.7 | 79.6 | 50.3 | 6 | 5
2026-06-24 | 12AM | 2 | 45 | 45 | 49 | 99.6 | 82.8 | 77.9 | 52.3 | 6 | 5
2026-06-24 | 6AM | 2 | 45 | 45 | 49.6 | 114.5 | 80.8 | 75.2 | 49.6 | 6 | 5
2026-06-24 | 8AM | 2 | 45 | 44.9 | 49.1 | 104.5 | 80.7 | 75.5 | 46.3 | 6 | 5
2026-06-24 | 2PM | 2 | 45 | 45 | 50 | 124.5 | 81.6 | 75.7 | 55.2 | 6 | 5
2026-06-24 | 4PM | 2 | 45 | 45 | 49.5 | 112 | 83.7 | 79.6 | 51 | 6 | 5
2026-06-24 | 10PM | 2 | 45 | 45 | 49.7 | 117 | 81.6 | 75.9 | 52.7 | 6 | 5
2026-06-25 | 2PM | 1 | 45 | 45 | 51.4 | 159.3 | 81 | 76 | 54.4 | Both | Both | Started @ 12:11p - take offline when load can be carried by one chiller
2026-06-25 | 4PM | 1 | 45 | 45 | 52 | 174.2 | 81 | 76 | 61 | Both | Both
2026-06-25 | 10PM | 1 | 45 | 45 | 52 | 174.2 | 82.2 | 76 | 62 | Both | Both
2026-06-25 | 12AM | 2 | 45 | 45 | 49.8 | 119.5 | 80.4 | 74.8 | 51.9 | 6 | 5
2026-06-25 | 6AM | 2 | 45 | 45 | 50.4 | 134.4 | 80 | 74 | 56.7 | 6 | 5
2026-06-25 | 8AM | 2 | 45 | 45 | 52.3 | 181.7 | 86.5 | 78.6 | 82.8 | 6 | 5
2026-06-25 | 2PM | 2 | 45 | 45 | 51.3 | 156.8 | 81.9 | 76 | 50.3 | Both | Both
2026-06-25 | 4PM | 2 | 45 | 45 | 51 | 149.3 | 81 | 76 | 50 | 6 | 6
2026-06-25 | 10PM | 2 | 45 | 43 | 48.8 | 144.4 | 85 | 79.8 | 54.5 | 6A | 5A
2026-06-26 | 12AM | 2 | 45 | 45 | 52.3 | 181.7 | 81 | 73.4 | 51.1 | 6 | 5
2026-06-26 | 6AM | 2 | 45 | 45 | 51.8 | 169.3 | 85.9 | 79.7 | 53.8 | 6 | 5
2026-06-26 | 2PM | 2 | 45 | 45 | 52.8 | 194.2 | 89.7 | 77.7 | 72.2 | 6 | 5
2026-06-26 | 4PM | 2 | 45 | 45 | 51.7 | 166.8 | 81.8 | 75.7 | 60.7 | 6 | 5
2026-06-26 | 10PM | 2 | 45 | 45 | 51.5 | 161.8 | 80.6 | 74.8 | 57.3 | 6 | 5
2026-06-27 | 12AM | 2 | 45 | 45 | 51.5 | 161.8 | 82.1 | 75.9 | 56.3 | 6 | 5
2026-06-27 | 6AM | 2 | 45 | 45 | 51.1 | 151.8 | 82 | 76.1 | 55.1 | 6 | 5
2026-06-27 | 8AM | 2 | 45 | 45 | 52 | 174.2 | 80.9 | 74.8 | 60 | 6 | 5
2026-06-27 | 2PM | 2 | 45 | 45 | 51.5 | 161.8 | 81.6 | 75.7 | 59.4 | 6 | 5
2026-06-27 | 4PM | 2 | 45 | 45 | 51.7 | 166.8 | 82.5 | 76.5 | 62.1 | 6 | 5
2026-06-27 | 10PM | 2 | 45 | 45 | 52 | 174.2 | 85 | 78 | 70.8 | 6 | 5
2026-06-28 | 12AM | 2 | 45 | 45 | 51.7 | 166.8 | 81.7 | 75.6 | 61.1 | 6 | 5
2026-06-28 | 6AM | 2 | 45 | 45 | 50.9 | 146.9 | 79.1 | 74.7 | 51.4 | 6 | 5
2026-06-28 | 8AM | 2 | 45 | 45 | 52 | 174.2 | 81 | 74.8 | 60.1 | 6 | 5
2026-06-28 | 2PM | 2 | 45 | 45 | 53.4 | 209.1 | 89.6 | 81.9 | 85.1 | 6 | 5
2026-06-28 | 4PM | 2 | 45 | 45 | 54 | 224 | 85 | 76 | 92 | 6 | 5
2026-06-28 | 10PM | 2 | 45 | 45 | 55 | 248.9 | 88 | 84 | 95 | 6 | 5
2026-06-29 | 8AM | 1 | 45 | 45.1 | 51.4 | 156.8 | 82.1 | 77.2 | 53.9 | BOTH | BOTH | Online @ 9:15 AM (12AM/6AM offline)
2026-06-29 | 2PM | 1 | 44 | 44 | 51.9 | 196.6 | 93.6 | 89.9 | 71.3 | BOTH | BOTH
2026-06-29 | 4PM | 1 | 44 | 44 | 51.8 | 194.2 | 89.4 | 83.3 | 69.4 | BOTH | BOTH
2026-06-29 | 10PM | 1 | 44 | 44 | 51 | 174.2 | 87.5 | 81.5 | 62.1 | BOTH | BOTH
2026-06-29 | 12AM | 2 | 45 | 45 | 52.9 | 196.6 | 90.1 | 82 | 90.3 | 6 | 5
2026-06-29 | 6AM | 2 | 45 | 45 | 52.1 | 176.7 | 86.4 | 79.2 | 76.8 | 6 | 5
2026-06-29 | 8AM | 2 | 45 | 45 | 52.2 | 179.2 | 88.4 | 80.7 | 85.1 | 6 | 5
2026-06-29 | 2PM | 2 | 44 | 44 | 51.7 | 191.7 | 91.1 | 83.7 | 70.2 | BOTH | BOTH
2026-06-29 | 4PM | 2 | 44 | 44 | 51.6 | 189.2 | 90.8 | 83.2 | 69.1 | BOTH | BOTH
2026-06-29 | 10PM | 2 | 44 | 44.1 | 51.1 | 174.2 | 87.5 | 80.9 | 61 | BOTH | BOTH
2026-06-30 | 12AM | 1 | 45 | 45 | 51.8 | 169.3 | 85.7 | 80.4 | 60.2 | 6,6A | 5,5A
2026-06-30 | 6AM | 1 | 45 | 45 | 52.3 | 181.7 | 88.3 | 82.6 | 64.8 | 6,6A | 5,5A
2026-06-30 | 8AM | 1 | 45 | 45 | 52.2 | 179.2 | 89.4 | 83.8 | 66.7 | BOTH | BOTH | Set point to 44 @ 9:30 AM
2026-06-30 | 2PM | 1 | 44 | 44 | 52 | 199.1 | 92.5 | 86.1 | 74.9 | BOTH | BOTH
2026-06-30 | 4PM | 1 | 44 | 44 | 52.1 | 201.6 | 92.8 | 84.3 | 75.7 | BOTH | BOTH
2026-06-30 | 10PM | 1 | 44 | 44 | 51.9 | 196.6 | 92.3 | 85.9 | 73.8 | BOTH | BOTH
2026-06-30 | 12AM | 2 | 45 | 45 | 51.7 | 166.8 | 86.8 | 80.5 | 57.5 | 6,6A | 5,5A
2026-06-30 | 6AM | 2 | 45 | 45 | 52.1 | 176.7 | 89.4 | 82.7 | 63.1 | 6,6A | 5,5A
2026-06-30 | 8AM | 2 | 45 | 45 | 52 | 174.2 | 90.5 | 83.8 | 63.6 | BOTH | BOTH | Set point to 44 @ 9:32 AM
2026-06-30 | 2PM | 2 | 44 | 44 | 51.8 | 194.2 | 93.5 | 86.1 | 74.3 | BOTH | BOTH
2026-06-30 | 4PM | 2 | 44 | 44 | 52 | 199.1 | 93.9 | 85.6 | 75.6 | BOTH | BOTH
2026-06-30 | 10PM | 2 | 44 | 44 | 51.7 | 191.7 | 93.5 | 86.1 | 73.2 | BOTH | BOTH
2026-07-01 | 12AM | 1 | 44 | 44 | 51.4 | 184.2 | 90 | 84.1 | 69.4 | BOTH | BOTH
2026-07-01 | 6AM | 1 | 44 | 44 | 51.3 | 181.7 | 89.5 | 83.7 | 68.2 | BOTH | BOTH
2026-07-01 | 8AM | 1 | 45 | 45 | 52.5 | 186.7 | 90.6 | 84.7 | 69.4 | BOTH | BOTH
2026-07-01 | 2PM | 1 | 43 | 43 | 51.5 | 211.6 | 93.6 | 86.7 | 80.5 | BOTH | BOTH
2026-07-01 | 4PM | 1 | 43 | 43 | 51.3 | 206.6 | 92.4 | 85.7 | 76.9 | BOTH | BOTH
2026-07-01 | 10PM | 1 | 43 | 43 | 50.4 | 184.2 | 88.5 | 82.7 | 67.7 | BOTH | BOTH
2026-07-01 | 12AM | 2 | 44 | 44 | 51.3 | 181.7 | 91.1 | 84.2 | 67.1 | BOTH | BOTH
2026-07-01 | 6AM | 2 | 44 | 44 | 51.2 | 179.2 | 90.6 | 83.8 | 65.9 | BOTH | BOTH
2026-07-01 | 8AM | 2 | 45 | 45 | 52.3 | 181.7 | 91.8 | 84.9 | 67.3 | BOTH | BOTH
2026-07-01 | 2PM | 2 | 43 | 43 | 51.4 | 209.1 | 94.9 | 86.9 | 81.4 | BOTH | BOTH
2026-07-01 | 4PM | 2 | 43 | 43 | 51.2 | 204.1 | 93.8 | 85.9 | 78.6 | BOTH | BOTH
2026-07-01 | 10PM | 2 | 43 | 43 | 50.3 | 181.7 | 89.7 | 82.8 | 66.5 | BOTH | BOTH
2026-07-02 | 12AM | 1 | 43 | 43 | 50.1 | 176.7 | 87.5 | 81.9 | 65.7 | Both | Both
2026-07-02 | 6AM | 1 | 43 | 43 | 50.1 | 176.7 | 87.5 | 81.9 | 65.3 | Both | Both
2026-07-02 | 8AM | 1 | 43 | 43 | 51.2 | 204.1 | 92.4 | 85.8 | 77.4 | Both | Both
2026-07-02 | 2PM | 1 | 43 | 43 | 51 | 199.1 | 93.1 | 86.9 | 74 | Both | Both
2026-07-02 | 4PM | 1 | 43 | 43 | 51.4 | 209.1 | 91.1 | 84.7 | 73.8 | Both | Both
2026-07-02 | 10PM | 1 | 43 | 43 | 50.8 | 194.2 | 90.4 | 84.3 | 71.7 | Both | Both
2026-07-02 | 12AM | 2 | 43 | 43 | 50 | 174.2 | 88.6 | 82 | 63.4 | Both | Both
2026-07-02 | 6AM | 2 | 43 | 43 | 49.9 | 171.8 | 88.6 | 82.1 | 62.8 | Both | Both
2026-07-02 | 8AM | 2 | 43 | 43 | 51 | 199.1 | 93.5 | 85.8 | 76.6 | Both | Both
2026-07-02 | 2PM | 2 | 43 | 43 | 51.1 | 201.6 | 93.3 | 85.6 | 76.8 | Both | Both
2026-07-02 | 4PM | 2 | 43 | 43 | 50.4 | 184.2 | 92.2 | 84.7 | 74 | Both | Both
2026-07-02 | 10PM | 2 | 43 | 43 | 50.6 | 189.2 | 91.7 | 84.5 | 71.2 | Both | Both
2026-07-03 | 12AM | 1 | 43 | 43 | 50.6 | 189.2 | 89.9 | 83.9 | 70 | Both | Both
2026-07-03 | 6AM | 1 | 43 | 43 | 49.9 | 171.8 | 86.5 | 81.1 | 64 | Both | Both
2026-07-03 | 8AM | 1 | 43 | 43 | 50.1 | 176.7 | 87.1 | 81.5 | 65.5 | Both | Both | reading taken 9AM (8AM crossed out); cw_leaving 87.1 operator-confirmed
2026-07-03 | 2PM | 1 | 43 | 43 | 50.8 | 194.2 | 88.5 | 82.4 | 70.1 | Both | Both
2026-07-03 | 4PM | 1 | 43 | 43 | 51.2 | 204.1 | 91.4 | 85.1 | 75.4 | Both | Both
2026-07-03 | 10PM | 1 | 43 | 43 | 49.6 | 164.3 | 83.1 | 78.3 | 67.9 | Both | Both | cw_entering 78.3 confirmed by operator (barely legible)
2026-07-03 | 12AM | 2 | 43 | 43 | 50.4 | 184.2 | 91.1 | 84 | 68.9 | Both | Both
2026-07-03 | 6AM | 2 | 43 | 43 | 49.8 | 169.3 | 87.7 | 81.3 | 60.9 | Both | Both | chw_entering 49.8 operator-confirmed
2026-07-03 | 8AM | 2 | 43 | 43 | 50 | 174.2 | 88.1 | 81.5 | 62.6 | Both | Both | reading taken 9AM (8AM crossed out)
2026-07-03 | 2PM | 2 | 43 | 43 | 50.4 | 184.2 | 89.7 | 82.5 | 69.4 | Both | Both
2026-07-03 | 4PM | 2 | 43 | 43 | 51.1 | 201.6 | 92.8 | 85.2 | 76.3 | Both | Both
2026-07-03 | 10PM | 2 | 43 | 43 | 49.5 | 161.8 | 84.3 | 78.2 | 55.1 | Both | Both
2026-07-04 | 12AM | 1 | 43 | 43 | 49.2 | 154.3 | 81.4 | 76 | 55.1 | Both | Both
2026-07-04 | 6AM | 1 | 43 | 43 | 49.2 | 154.3 | 81.8 | 76.9 | 55.5 | Both | Both
2026-07-04 | 8AM | 1 | 43 | 43 | 49.6 | 164.3 | 83.8 | 78.7 | 59.1 | Both | Both
2026-07-04 | 2PM | 1 | 43 | 43 | 50.1 | 176.7 | 86.1 | 80.5 | 64 | Both | Both
2026-07-04 | 4PM | 1 | 43 | 43 | 50 | 174.2 | 87.7 | 81.9 | 66 | Both | Both | pumps Both per operator (boxes unmarked/checked on sheet)
2026-07-04 | 10PM | 1 | 43 | 43 | 49.8 | 169.3 | 84.9 | 79.6 | 66.4 | Both | Both | pumps Both per operator; chw_supply read 65 (sheet glyph resembles 45; Ch#2 evening also 65) - confirm
2026-07-04 | 12AM | 2 | 43 | 43 | 49.1 | 151.8 | 82.4 | 76.7 | 50.7 | Both | Both
2026-07-04 | 6AM | 2 | 43 | 43 | 49.1 | 151.8 | 82.8 | 77.1 | 51.3 | Both | Both
2026-07-04 | 8AM | 2 | 43 | 43 | 49.4 | 159.3 | 84.9 | 78.9 | 55.2 | Both | Both | reading taken 9AM (8AM crossed out)
2026-07-04 | 2PM | 2 | 43 | 43 | 49.9 | 171.8 | 87.1 | 80.5 | 61.3 | Both | Both
2026-07-04 | 4PM | 2 | 43 | 43 | 50 | 174.2 | 88 | 81.9 | 65 | Both | Both | pumps Both per operator (checkmarks on sheet = all pumps on)
2026-07-04 | 10PM | 2 | 43 | 43 | 49.7 | 166.8 | 86 | 79.7 | 58 | Both | Both | pumps Both per operator (checkmarks on sheet = all pumps on)
2026-07-05 | 12AM | 1 | 43 | 43 | 49.7 | 166.8 | 84.5 | 79.2 | 60.7 | Both | Both
2026-07-05 | 6AM | 1 | 43 | 43 | 49.3 | 156.8 | 82.4 | 77.5 | 56.7 | Both | Both
2026-07-05 | 8AM | 1 | 43 | 43 | 49.4 | 159.3 | 83 | 78.1 | 57.9 | Both | Both
2026-07-05 | 2PM | 1 | 45 | 45 | 51.1 | 151.8 | 84.1 | 79.4 | 56.2 | Both | Both | reading ~2:30p; SP raised 43->44 @2p, ->45 @2:10p
2026-07-05 | 4PM | 1 | 45 | 45 | 51.7 | 166.8 | 85.4 | 80.2 | 47.3 | Both | Both
2026-07-05 | 10PM | 1 | 45 | 45 | 51.3 | 156.8 | 83.1 | 78.3 | 57.1 | Both | Both
2026-07-05 | 12AM | 2 | 43 | 43 | 49.5 | 161.8 | 85.5 | 79.4 | 57 | Both | Both
2026-07-05 | 6AM | 2 | 43 | 43 | 49.2 | 154.3 | 83.4 | 77.6 | 52.4 | Both | Both
2026-07-05 | 8AM | 2 | 43 | 43 | 49.3 | 156.8 | 84.1 | 78.2 | 53.5 | Both | Both
2026-07-05 | 2PM | 2 | 45 | 44.5 | 51.1 | 164.3 | 85.6 | 79.6 | 55.2 | Both | Both | reading ~2:30p; SP raised 43->44 @2:10p, ->45 @2:30p
2026-07-05 | 4PM | 2 | 45 | 45 | 51.5 | 161.8 | 86.6 | 80.5 | 55.8 | Both | Both
2026-07-05 | 10PM | 2 | 45 | 45 | 51.1 | 151.8 | 84.2 | 78.4 | 51.2 | Both | Both
2026-07-06 | 12AM | 1 | 45 | 45 | 50.9 | 146.9 | 81 | 76.5 | 51.6 | Both | Both | Closed CW & CHW valves on Chiller #2
2026-07-06 | 6AM | 1 | 45 | 45 | 54.1 | 226.5 | 83 | 75.2 | 42.9 | 6 | 5A
2026-07-06 | 8AM | 1 | 45 | 45 | 52.4 | 184.2 | 83.2 | 76.5 | 73 | 6 | 5A
2026-07-06 | 2PM | 1 | 45 | 45 | 53.8 | 219 | 88.6 | 80.5 | 91.2 | 6 | 5A
2026-07-06 | 4PM | 1 | 45 | 48 | 53 | 124.5 | 87 | 80 | 91 | 6 | 5A | CHW leaving 48 > SP45 — #1 maxed, lead swapped to #2
2026-07-06 | 12AM | 2 | 45 | 45 | 50.8 | 144.4 | 82 | 76.6 | 44.6 | Both | Both | Off @ 2am; #6A CHW pump / #5 condenser pump
2026-07-06 | 10PM | 2 | 45 | 45 | 54 | 224 | 88.2 | 78 | 72.9 | 6 | 5A | Lead swapped back to #2; #1 off
2026-07-07 | 2PM | 1 | 45 | 45 | 51.7 | 166.8 | 85 | 79.8 | 59.2 | Both | Both | On @ 11AM
2026-07-07 | 4PM | 1 | 45 | 45 | 51.9 | 171.8 | 86.6 | 80.9 | 68 | Both | Both
2026-07-07 | 10PM | 1 | 45 | 45 | 53.2 | 204.1 | 88.8 | 82.3 | 76.4 | Both | Both | On @ 11AM day; 10PM cond lv/ent operator-confirmed 88.8/82.3
2026-07-07 | 12AM | 2 | 45 | 45 | 52.5 | 186.7 | 82.9 | 74.6 | 57.3 | 6 | 5A
2026-07-07 | 6AM | 2 | 45 | 45 | 51.9 | 171.8 | 82.2 | 74.4 | 51.4 | 6 | 5A
2026-07-07 | 8AM | 2 | 45 | 45 | 55.2 | 253.9 | 89.1 | 80.9 | 90 | 6 | 5A | read ~9:30
2026-07-07 | 2PM | 2 | 45 | 45 | 51.6 | 164.3 | 87 | 80.1 | 62 | Both | Both
2026-07-07 | 4PM | 2 | 45 | 45 | 51.8 | 169.3 | 87.8 | 81.1 | 61 | Both | Both
2026-07-07 | 10PM | 2 | 45 | 45 | 53.1 | 201.6 | 90.1 | 82.5 | 71 | Both | Both
2026-07-08 | 12AM | 1 | 45 | 45 | 52.8 | 194.2 | 87 | 80.9 | 44.4 | Both | Both
2026-07-08 | 6AM | 1 | 45 | 45 | 52.3 | 181.7 | 85.1 | 79.4 | 62.3 | Both | Both
2026-07-08 | 8AM | 1 | 45 | 45 | 52.8 | 194.2 | 87.2 | 81.1 | 66.4 | Both | Both
2026-07-08 | 2PM | 1 | 45 | 45 | 51.2 | 154.3 | 81.1 | 76.1 | 54.2 | Both | Both
2026-07-08 | 4PM | 1 | 45 | 45 | 51.2 | 154.3 | 80.9 | 76 | 53.6 | Both | Both | Chiller #1 taken offline at 8PM — no 10PM reading; #2 carried the load solo after.
2026-07-08 | 12AM | 2 | 45 | 45 | 52.6 | 189.2 | 88.5 | 81 | 65.9 | Both | Both
2026-07-08 | 6AM | 2 | 45 | 45 | 52.2 | 179.2 | 86.3 | 79.6 | 60.7 | Both | Both
2026-07-08 | 8AM | 2 | 45 | 45 | 52.7 | 191.7 | 88.5 | 81.2 | 47 | Both | Both
2026-07-08 | 2PM | 2 | 45 | 45 | 51.1 | 151.8 | 82.3 | 76.3 | 51.9 | Both | Both
2026-07-08 | 4PM | 2 | 45 | 45 | 51 | 149.3 | 82.1 | 76.2 | 50.6 | Both | Both
2026-07-08 | 10PM | 2 | 45 | 45 | 51.3 | 156.8 | 83.1 | 76 | 70.2 | Both | Both
2026-07-09 | 8AM | 1 | 45 | 45 | 52.8 | 194.2 | 86.5 | 80.4 | 65.5 | Both | Both | Started 6:20AM
2026-07-09 | 2PM | 1 | 45 | 45 | 52 | 174.2 | 86.5 | 80.8 | 64 | Both | Both
2026-07-09 | 4PM | 1 | 45 | 45 | 51.9 | 171.8 | 85.9 | 80.3 | 61.9 | Both | Both
2026-07-09 | 10PM | 1 | 45 | 45 | 52.6 | 189.2 | 88.3 | 80.4 | 64.1 | Both | Both
2026-07-09 | 12AM | 2 | 45 | 44.9 | 52.8 | 196.6 | 84.7 | 76.1 | 93 | 6 | 5
2026-07-09 | 6AM | 2 | 45 | 45.1 | 54.3 | 229 | 88.1 | 79.5 | 99.8 | 6 | 5 | #2 solo overnight; #1 started 6:20AM
2026-07-09 | 8AM | 2 | 45 | 45 | 52.5 | 186.7 | 87.6 | 80.5 | 64.4 | Both | Both
2026-07-09 | 2PM | 2 | 45 | 45 | 51.8 | 169.3 | 87.7 | 80.9 | 62.5 | Both | Both
2026-07-09 | 4PM | 2 | 45 | 45 | 51.9 | 171.8 | 87.2 | 80.6 | 61.2 | Both | Both
2026-07-09 | 10PM | 2 | 45 | 45 | 52.6 | 189.2 | 87.6 | 80.5 | 64.7 | Both | Both
2026-07-10 | 12AM | 1 | 45 | 45 | 52.4 | 184.2 | 85.6 | 79.8 | 62.2 | Both | Both
2026-07-10 | 6AM | 1 | 45 | 45 | 51.7 | 166.8 | 82.3 | 77.3 | 55.7 | Both | Both
2026-07-10 | 8AM | 1 | 45 | 45 | 52.4 | 184.2 | 82.5 | 77.4 | 56.2 | 6A | Both | 8AM: dropped to one CHW pump
2026-07-10 | 2PM | 1 | 44 | 44 | 52.2 | 204.1 | 86.2 | 80.5 | 64.1 | 6A | Both | SP lowered 45→44 at 10:41 AM (leaving temp follows)
2026-07-10 | 4PM | 1 | 44 | 44 | 52.3 | 206.6 | 87.9 | 82 | 66.3 | 6A | Both
2026-07-10 | 10PM | 1 | 44 | 44 | 52.5 | 211.6 | 87.8 | 80.7 | 64.5 | 6A | Both
2026-07-10 | 12AM | 2 | 45 | 45 | 52.3 | 181.7 | 86.8 | 79.9 | 61.7 | Both | Both
2026-07-10 | 6AM | 2 | 45 | 45 | 51.6 | 164.3 | 83.6 | 77.4 | 53.5 | Both | Both
2026-07-10 | 8AM | 2 | 45 | 45 | 52.3 | 181.7 | 83.8 | 77.1 | 53.6 | 6A | Both
2026-07-10 | 2PM | 2 | 44 | 44 | 52 | 199.1 | 87.6 | 80.6 | 64.5 | 6A | Both | SP lowered 45→44 at 10:41 AM (leaving temp follows)
2026-07-10 | 4PM | 2 | 44 | 44 | 52.2 | 204.1 | 89.4 | 82.2 | 68.2 | 6A | Both
2026-07-10 | 10PM | 2 | 44 | 44 | 52.4 | 209.1 | 88.2 | 80.9 | 67.2 | 6A | Both
2026-07-11 | 12AM | 1 | 44.3 | 44.3 | 52.1 | 194.2 | 83 | 77.8 | 58.1 | 6A | Both | ACTIVE SETPOINT ON, CHW RESET OFF — setpoint floats per slot
2026-07-11 | 6AM | 1 | 47.2 | 47.2 | 52.1 | 122 | 84.9 | 81.5 | 48.9 | 6A | Both
2026-07-11 | 8AM | 1 | 44 | 44 | 50.9 | 171.8 | 82.7 | 77.9 | 55.1 | 6A | Both
2026-07-11 | 2PM | 1 | 45 | 45 | 50.8 | 144.4 | 84.9 | 80.8 | 53.9 | 6A | Both
2026-07-11 | 4PM | 1 | 45 | 45 | 51.4 | 159.3 | 80.7 | 76.2 | 50 | 6A | Both
2026-07-11 | 10PM | 1 | 48 | 48 | 51.1 | 77.2 | 85.4 | 81.2 | 53.7 | 6A | Both
2026-07-11 | 12AM | 2 | 44.7 | 44.6 | 51.9 | 181.7 | 84.2 | 78 | 55 | 6A | Both | ACTIVE SETPOINT ON, CHW RESET OFF — setpoint floats per slot
2026-07-11 | 6AM | 2 | 45.5 | 45.4 | 51.9 | 161.8 | 87.2 | 81.7 | 52.5 | 6A | Both
2026-07-11 | 8AM | 2 | 44 | 43.6 | 50.7 | 176.7 | 85.9 | 79.2 | 55.1 | 6A | Both
2026-07-11 | 2PM | 2 | 45 | 44.9 | 50.7 | 144.4 | 85.7 | 80.6 | 50.2 | 6A | Both
2026-07-11 | 4PM | 2 | 45 | 45 | 51.3 | 156.8 | 80.7 | 76.3 | 49.8 | 6A | Both
2026-07-11 | 10PM | 2 | 45 | 45 | 50.9 | 146.9 | 85.8 | 80.5 | 50.5 | 6A | Both
2026-07-12 | 8AM | 1 | 45 | 45.1 | 53.4 | 206.6 | 83.2 | 77.7 | 58.4 | Both | 5A,5 | Started 9:50am; reading taken 10AM
2026-07-12 | 2PM | 1 | 45 | 45 | 50.2 | 129.4 | 80 | 75.5 | 49.4 | Both | 5A,5
2026-07-12 | 12AM | 2 | 45 | 45 | 50.5 | 136.9 | 80.2 | 74.2 | 58.5 | 6A | 5A | Adj setpoint 45
2026-07-12 | 6AM | 2 | 45 | 45 | 51.6 | 164.3 | 82.4 | 75.5 | 69.7 | 6A | 5A
2026-07-12 | 8AM | 2 | 45 | 45 | 53 | 199.1 | 87.8 | 79.7 | 87.8 | 6A | 5A
2026-07-12 | 2PM | 2 | 45 | 44.1 | 49.9 | 144.4 | 83.1 | 76.7 | 47.6 | Both | 5A,5
2026-07-12 | 4PM | 2 | 45 | 45 | 53 | 199.1 | 88.5 | 79.7 | 86.9 | 6A | 5A,5
2026-07-12 | 10PM | 2 | 45 | 45 | 52.4 | 184.2 | 85.5 | 77.2 | 76 | 6A | 5
2026-07-13 | 6AM | 1 | 45 | 45 | 49.9 | 122 | 85 | 81.1 | 52.6 | Both | Both
2026-07-13 | 8AM | 1 | 45 | 45 | 54.5 | 236.5 | 86.3 | 78.4 | 81.7 | 6A | 5 | reading taken 9AM
2026-07-13 | 2PM | 1 | 45 | 45.1 | 55.3 | 253.9 | 86.5 | 76.9 | 99 | 6A | 5
2026-07-13 | 4PM | 1 | 45 | 45 | 51.7 | 166.8 | 84.4 | 76.5 | 58.9 | Both | Both
2026-07-13 | 10PM | 1 | 45 | 45 | 51.6 | 164.3 | 85.2 | 80 | 52.8 | Both | Both
2026-07-13 | 12AM | 2 | 45 | 45 | 51.5 | 161.8 | 82.3 | 75.9 | 44 | 6A | 5 | Active setpoint on; off ~8am, cycled back on 2:30pm (2PM reading not taken)
2026-07-13 | 6AM | 2 | 43 | 43 | 49.8 | 169.3 | 89.5 | 81.2 | 59.5 | Both | Both
2026-07-13 | 8AM | 2 | 45 | 45 | 51.6 | 164.3 | 81.8 | 76.2 | 59.4 | Both | Both
2026-07-13 | 4PM | 2 | 45 | 45 | 51.6 | 164.3 | 87.8 | 82.7 | 59.3 | Both | Both
2026-07-13 | 10PM | 2 | 45 | 45 | 51.6 | 164.3 | 87.8 | 80.2 | 58.8 | Both | Both

## BMS Snapshots
Date | Time | Event | Calc Load (t) | MA Enthalpy | Heat Loop Sup | Heat Loop Ret | Heat Loop BTU/h
2026-06-09 | 07:00 | tsv_backfill | 234 | 28.25 | 120.09 | 113 | 797625
2026-06-09 | 15:00 | tsv_backfill | 370.2 | 31.3 | 120.09 | 113.37 | 756000
2026-06-09 | 23:00 | tsv_backfill | 359.8 | 31.04 | 120.09 | 111.97 | 913500
2026-06-10 | 07:00 | tsv_backfill | 310.9 | 28.97 | 121.03 | 112.34 | 977625
2026-06-10 | 15:00 | tsv_backfill | 408.7 | 32.52 | 121.03 | 115.15 | 661500
2026-06-10 | 23:00 | tsv_backfill | 418.6 | 32.87 | 121.03 | 111.13 | 1113750
2026-06-11 | 07:00 | tsv_backfill | 324.5 | 29 | 118.41 | 112.25 | 693000
2026-06-11 | 15:00 | tsv_backfill | 346 | 30.1 | 118.41 | 114.31 | 461250
2026-06-11 | 23:00 | tsv_backfill | 420.7 | 32.96 | 118.41 | 114.12 | 482625
2026-06-12 | 07:00 | tsv_backfill | 282.4 | 27.89 | 121.21 | 114.49 | 756000
2026-06-12 | 15:00 | tsv_backfill | 258.8 | 27.49 | 121.21 | 111.6 | 1081125
2026-06-12 | 23:00 | tsv_backfill | 260.5 | 28.57 | 121.21 | 112.25 | 1008000
2026-06-13 | 07:00 | tsv_backfill | 156.9 | 25.42 | 131.63 | 119.91 | 1318500
2026-06-13 | 15:00 | tsv_backfill | 277.6 | 28.45 | 121.4 | 111.6 | 1102500
2026-06-13 | 23:00 | tsv_backfill | 286.6 | 29.7 | 121.4 | 114.96 | 724500
2026-06-14 | 07:00 | tsv_backfill | 250.5 | 28 | 121.12 | 113.74 | 830250
2026-06-14 | 15:00 | tsv_backfill | 250.3 | 27.1 | 131.63 | 120.75 | 1224000
2026-06-14 | 23:00 | tsv_backfill | 193.8 | 25.29 | 141.83 | 128.36 | 1515375
2026-06-15 | 07:00 | tsv_backfill | 117 | 21.72 | 156.83 | 143.46 | 1504125
2026-06-15 | 15:00 | tsv_backfill | 147.1 | 22.99 | 121.03 | 113.09 | 893250
2026-06-15 | 23:00 | tsv_backfill | 160.8 | 24.29 | 136.44 | 125.67 | 1211625
2026-06-16 | 07:00 | tsv_backfill | 141.6 | 22.03 | 146.63 | 133.94 | 1427625
2026-06-16 | 08:36 | historical_data_panel | 86.2 | 23.65 | 136 | 124 | 1350000
2026-06-16 | 11:56 | historical_data_panel | 189.3 | 26.5 | 121 | 113 | 900000
2026-06-16 | 15:00 | tsv_backfill | 172.6 | 24.94 | 121.12 | 113.56 | 850500
2026-06-16 | 23:00 | tsv_backfill | 160.1 | 25 | 131.15 | 119.16 | 1348875
2026-06-17 | 07:00 | tsv_backfill | 140.4 | 23.29 | 140.84 | 129.53 | 1272375
2026-06-17 | 15:00 | tsv_backfill | 183.6 | 25.1 | 127.9 | 117.75 | 1141875
2026-06-17 | 23:00 | tsv_backfill | 133.5 | 25.2 | 129.32 | 115.46 | 1559250
2026-06-18 | 07:00 | tsv_backfill | 201.2 | 25.6 | 122.69 | 114.68 | 901125
2026-06-18 | 15:00 | tsv_backfill | 227.6 | 25.84 | 117.85 | 111.69 | 693000
2026-06-18 | 23:00 | tsv_backfill | 172.9 | 25.69 | 138.46 | 126.54 | 1341000
2026-06-19 | 07:00 | tsv_backfill | 145.5 | 23.29 | 151.92 | 141.63 | 1157625
2026-06-19 | 15:00 | tsv_backfill | 168.7 | 25.61 | 121.12 | 112.44 | 976500
2026-06-19 | 23:00 | tsv_backfill | 178 | 26 | 126.25 | 118.6 | 860625
2026-06-20 | 07:00 | tsv_backfill | 139.7 | 23.11 | 141.54 | 130.38 | 1255500
2026-06-20 | 15:00 | tsv_backfill | 171.6 | 25.84 | 121.21 | 112.62 | 966375
2026-06-20 | 23:00 | tsv_backfill | 175.6 | 26.5 | 126.25 | 117.57 | 976500
2026-06-21 | 07:00 | tsv_history_import | 147.9 | 23.56 | 145.74 | 133.02 | 1431000
2026-06-21 | 07:35 | historical_cooling_low_load | 84.7 | 23.85 | 149 | 135 | 1575000
2026-06-21 | 15:00 | tsv_backfill | 206 | 26.02 | 120.75 | 111.78 | 1009125
2026-06-21 | 23:00 | tsv_backfill | 198.5 | 26.11 | 136.54 | 122.5 | 1579500
2026-06-22 | 07:00 | tsv_backfill | 142.9 | 23.56 | 148.94 | 134.61 | 1612125
2026-06-22 | 15:00 | tsv_backfill | 198.6 | 24.63 | 121.12 | 111.32 | 1102500
2026-06-22 | 23:00 | tsv_backfill | 199.5 | 26.73 | 131.63 | 120.84 | 1213875
2026-06-23 | 07:00 | tsv_backfill | 121.4 | 23.61 | 162.31 | 148.27 | 1579500
2026-06-23 | 15:00 | tsv_backfill | 181.9 | 25.75 | 141.25 | 130.29 | 1233000
2026-06-23 | 23:00 | tsv_backfill | 183.2 | 26.58 | 151.06 | 137.98 | 1471500
2026-06-24 | 07:00 | tsv_backfill | 148.5 | 23.34 | 167.71 | 156.34 | 1279125
2026-06-24 | 15:00 | tsv_backfill | 174.6 | 25.96 | 141.34 | 131.73 | 1081125
2026-06-24 | 23:00 | tsv_backfill | 169.2 | 25.94 | 141.34 | 132.5 | 994500
2026-06-25 | 07:00 | tsv_backfill | 145.2 | 24.76 | 156.63 | 142.5 | 1589625
2026-06-25 | 15:00 | tsv_backfill | 236.9 | 26.61 | 121.03 | 111.32 | 1092375
2026-06-25 | 23:00 | tsv_backfill | 272.7 | 29.04 | 121.03 | 113.37 | 861750
2026-06-26 | 07:00 | tsv_backfill | 137.8 | 24.21 | 146.63 | 132.88 | 1546875
2026-06-26 | 15:00 | tsv_backfill | 214.8 | 26.04 | 121.12 | 110.76 | 1165500
2026-06-26 | 23:00 | tsv_backfill | 215.7 | 26.43 | 131.54 | 119.91 | 1308375
2026-06-27 | 07:00 | tsv_backfill | 142.7 | 24.45 | 146.54 | 133.17 | 1504125
2026-06-27 | 15:00 | tsv_backfill | 235.2 | 26.64 | 120.56 | 110.85 | 1092375
2026-06-27 | 23:00 | tsv_backfill | 257.4 | 28.48 | 120.56 | 110.01 | 1186875
2026-06-28 | 07:00 | tsv_backfill | 152.2 | 25.07 | 135.96 | 123.46 | 1406250
2026-06-28 | 15:00 | tsv_backfill | 261.7 | 27.76 | 120.56 | 111.04 | 1071000
2026-06-28 | 23:00 | tsv_backfill | 312.5 | 30.33 | 120.56 | 112.81 | 871875
2026-06-29 | 07:00 | tsv_backfill | 239 | 26.71 | 80.23 | 77.71 | 283500
2026-06-29 | 15:00 | tsv_backfill | 332.7 | 29.1 | 80.23 | 76.47 | 423000
2026-06-29 | 23:00 | tsv_backfill | 376.9 | 30.44 | 80.23 | 76.75 | 391500
2026-06-30 | 07:00 | tsv_backfill | 320.7 | 29.11 | 79.29 | 75.66 | 408375
2026-06-30 | 15:00 | tsv_backfill | 389.7 | 30.7 | 79.29 | 77.33 | 220500
2026-06-30 | 23:00 | tsv_backfill | 418.8 | 31.46 | 79.29 | 76.11 | 357750
2026-07-01 | 07:00 | tsv_history_import | 355 | 29.39 | 80.6 | 76.13 | 502875
2026-07-01 | 08:00 | tsv_history_import | 340.2 | 29.53 | 80.79 | 76.25 | 510750
2026-07-01 | 08:29 | baseline_before_hhw_min_80_to_100 | 352.9 | 30.57 | 81 | 77 | 450000
2026-07-01 | 09:00 | tsv_history_import | 364 | 30.13 | 90.37 | 83.66 | 754875
2026-07-01 | 10:00 | tsv_history_import | 399.7 | 31.31 | 97.83 | 91.77 | 681750
2026-07-01 | 10:03 | after_hhw_min_decreased_100_to_90 | 399 | 32.09 | 91 | 84 | 787500
2026-07-01 | 11:00 | tsv_history_import | 407.4 | 31.47 | 86.43 | 81.31 | 576000
2026-07-01 | 12:00 | tsv_history_import | 436.2 | 32.28 | 80.88 | 76.3 | 515250
2026-07-01 | 13:00 | tsv_history_import | 430.1 | 32.18 | 80.88 | 76.49 | 493875
2026-07-01 | 14:00 | tsv_history_import | 454.3 | 32.82 | 74.56 | 70.95 | 406125
2026-07-01 | 15:00 | tsv_backfill | 410.2 | 31.52 | 70.86 | 67.59 | 367875
2026-07-01 | 16:00 | tsv_history_import | 464.3 | 32.6 | 70.86 | 67.8 | 344250
2026-07-01 | 17:00 | tsv_history_import | 439 | 31.88 | 70.86 | 67.82 | 342000
2026-07-01 | 18:00 | tsv_history_import | 452.4 | 31.88 | 70.86 | 67.95 | 327375
2026-07-01 | 19:00 | tsv_history_import | 444.9 | 31.57 | 70.86 | 67.72 | 353250
2026-07-01 | 20:00 | tsv_history_import | 407.4 | 30.57 | 70.86 | 67.56 | 371250
2026-07-01 | 21:00 | tsv_history_import | 396.3 | 30.32 | 70.86 | 67.74 | 351000
2026-07-01 | 22:00 | tsv_history_import | 385.5 | 29.99 | 70.86 | 67.69 | 356625
2026-07-01 | 23:00 | tsv_backfill | 418.6 | 31.01 | 70.86 | 67.41 | 388125
2026-07-02 | 00:00 | tsv_history_import | 371.6 | 29.26 | 70.86 | 67.52 | 375750
2026-07-02 | 01:00 | tsv_history_import | 353.6 | 28.88 | 69.41 | 67.37 | 229500
2026-07-02 | 02:00 | tsv_history_import | 357.3 | 29.04 | 69.41 | 67.47 | 218250
2026-07-02 | 03:00 | tsv_history_import | 337.4 | 28.41 | 69.41 | 67.49 | 216000
2026-07-02 | 04:00 | tsv_history_import | 354 | 28.88 | 69.41 | 67.44 | 221625
2026-07-02 | 05:00 | tsv_history_import | 336.6 | 28.39 | 69.41 | 67.36 | 230625
2026-07-02 | 06:00 | tsv_history_import | 335 | 28.39 | 69.41 | 67.3 | 237375
2026-07-02 | 07:00 | tsv_history_import | 327.5 | 28.03 | 73.43 | 69.37 | 456750
2026-07-02 | 07:49 | after_hhw_min_raised_90_to_95 | 330.5 | 28.96 | 97 | 89 | 900000
2026-07-02 | 08:00 | tsv_history_import | 333.1 | 28.37 | 95.53 | 87.62 | 889875
2026-07-02 | 09:00 | tsv_history_import | 358.9 | 29.33 | 96.66 | 88.96 | 866250
2026-07-02 | 10:00 | tsv_history_import | 390.1 | 30.25 | 88.85 | 83.71 | 578250
2026-07-02 | 10:42 | hhw_study_midmorning_hot | 398.8 | 31.39 | 87 | 80 | 787500
2026-07-02 | 11:00 | tsv_history_import | 407 | 30.92 | 86.58 | 80.6 | 672750
2026-07-02 | 12:00 | tsv_history_import | 425.9 | 31.63 | 76.03 | 72.32 | 417375
2026-07-02 | 13:00 | tsv_history_import | 415 | 31.39 | 71.58 | 66.99 | 516375
2026-07-02 | 14:00 | tsv_history_import | 419.9 | 31.52 | 71.58 | 67.88 | 416250
2026-07-02 | 14:04 | hhw_study_afternoon_peak_hot | 420.2 | 31.99 | 72 | 67 | 562500
2026-07-02 | 15:00 | tsv_history_import | 431 | 32.1 | 71.58 | 67.7 | 436500
2026-07-02 | 16:00 | tsv_history_import | 430.6 | 31.66 | 71.58 | 67.75 | 430875
2026-07-02 | 17:00 | tsv_history_import | 419.4 | 31.19 | 71.58 | 67.85 | 419625
2026-07-02 | 18:00 | tsv_history_import | 426.5 | 31.19 | 71.58 | 67.73 | 433125
2026-07-02 | 19:00 | tsv_history_import | 426.8 | 31.19 | 71.58 | 67.59 | 448875
2026-07-02 | 20:00 | tsv_history_import | 424.1 | 31.16 | 71.58 | 67.84 | 420750
2026-07-02 | 21:00 | tsv_history_import | 401.9 | 30.57 | 71.58 | 67.71 | 435375
2026-07-02 | 22:00 | tsv_history_import | 395.3 | 30.29 | 71.58 | 67.64 | 443250
2026-07-02 | 23:00 | tsv_backfill | 412.9 | 30.9 | 71.58 | 67.87 | 417375
2026-07-03 | 00:00 | tsv_history_import | 378.4 | 29.83 | 71.58 | 67.44 | 465750
2026-07-03 | 01:00 | tsv_history_import | 370.2 | 29.49 | 71.22 | 67.62 | 405000
2026-07-03 | 02:00 | tsv_history_import | 361.3 | 29.32 | 71.22 | 67.54 | 414000
2026-07-03 | 03:00 | tsv_history_import | 370.6 | 29.54 | 71.22 | 67.49 | 419625
2026-07-03 | 04:00 | tsv_history_import | 360.3 | 29.13 | 71.22 | 67.42 | 427500
2026-07-03 | 05:00 | tsv_history_import | 356.7 | 29.16 | 71.22 | 67.37 | 433125
2026-07-03 | 06:00 | tsv_history_import | 339.7 | 28.4 | 71.22 | 67.34 | 436500
2026-07-03 | 06:58 | morning_shift1 | 332.6 | 28.52 | 71 | 67 | 450000
2026-07-03 | 07:00 | tsv_history_import | 343.8 | 28.38 | 71.22 | 67.29 | 442125
2026-07-03 | 07:32 | ebi_xps_import | 338.9 | 28.3 | 87.32 | 85.18 | 240750
2026-07-03 | 08:00 | tsv_history_import | 339.8 | 28.3 | 87.55 | 82.36 | 583875
2026-07-03 | 09:00 | tsv_history_import | 355.7 | 28.7 | 97.5 | 88.67 | 993375
2026-07-03 | 10:00 | tsv_history_import | 376.5 | 29.29 | 97.5 | 88.74 | 985500
2026-07-03 | 11:00 | tsv_history_import | 388.2 | 29.72 | 97.5 | 92.96 | 510750
2026-07-03 | 11:21 | ebi_xps_import | 386 | 30.04 | 97.5 | 93.77 | 419625
2026-07-03 | 12:00 | tsv_history_import | 393.6 | 30.22 | 97.5 | 93.18 | 486000
2026-07-03 | 13:00 | tsv_history_import | 397.2 | 30.45 | 97.5 | 93.26 | 477000
2026-07-03 | 14:00 | tsv_history_import | 417.8 | 31.1 | 97.5 | 93.35 | 466875
2026-07-03 | 14:02 | ebi_xps_import | 433.7 | 31.37 | 97.5 | 93.77 | 419625
2026-07-03 | 15:00 | tsv_history_import | 432 | 31.37 | 97.5 | 93.61 | 437625
2026-07-03 | 16:00 | tsv_history_import | 445.5 | 31.8 | 97.5 | 93.83 | 412875
2026-07-03 | 17:00 | tsv_history_import | 451.4 | 32.13 | 97.5 | 93.96 | 398250
2026-07-03 | 18:00 | tsv_history_import | 443.9 | 32.13 | 97.5 | 94.08 | 384750
2026-07-03 | 19:00 | tsv_history_import | 350.5 | 29.7 | 97.5 | 94.1 | 382500
2026-07-03 | 20:00 | tsv_history_import | 315.4 | 27.65 | 97.5 | 93.55 | 444375
2026-07-03 | 21:00 | tsv_history_import | 305 | 27.11 | 97.5 | 93.21 | 482625
2026-07-03 | 22:00 | tsv_history_import | 302.9 | 27.21 | 97.5 | 93.25 | 478125
2026-07-03 | 23:00 | tsv_backfill | 361.5 | 29.23 | 97.5 | 91.71 | 651375
2026-07-04 | 00:00 | tsv_history_import | 281.1 | 26.57 | 97.5 | 92.96 | 510750
2026-07-04 | 01:00 | tsv_history_import | 293.4 | 26.6 | 98.62 | 92.75 | 660375
2026-07-04 | 02:00 | tsv_history_import | 291.5 | 26.4 | 98.62 | 92.72 | 663750
2026-07-04 | 03:00 | tsv_history_import | 292 | 26.39 | 98.62 | 92.78 | 657000
2026-07-04 | 04:00 | tsv_history_import | 290.5 | 26.39 | 98.62 | 92.78 | 657000
2026-07-04 | 05:00 | tsv_history_import | 283.9 | 26.39 | 98.62 | 92.76 | 659250
2026-07-04 | 06:00 | tsv_history_import | 274.8 | 26.07 | 98.62 | 92.73 | 662625
2026-07-04 | 07:00 | tsv_history_import | 286.5 | 26.23 | 99.01 | 92.75 | 704250
2026-07-04 | 07:02 | ebi_xps_import | 286.7 | 26.23 | 102.54 | 93.39 | 1029375
2026-07-04 | 08:00 | tsv_history_import | 287.3 | 26.29 | 104.56 | 94.54 | 1127250
2026-07-04 | 09:00 | tsv_history_import | 296.7 | 26.83 | 104.81 | 97.09 | 868500
2026-07-04 | 10:00 | tsv_history_import | 306.1 | 27.13 | 102.54 | 96.9 | 634500
2026-07-04 | 11:00 | tsv_history_import | 340.8 | 28.07 | 102.54 | 97.03 | 619875
2026-07-04 | 12:00 | tsv_history_import | 355.7 | 28.8 | 102.54 | 97.13 | 608625
2026-07-04 | 13:00 | tsv_history_import | 354.5 | 29.12 | 102.54 | 97.21 | 599625
2026-07-04 | 14:00 | tsv_history_import | 371.9 | 29.56 | 102.54 | 97.29 | 590625
2026-07-04 | 14:16 | ebi_xps_import | 365.7 | 29.34 | 102.54 | 98.34 | 472500
2026-07-04 | 15:00 | tsv_history_import | 364.4 | 29.35 | 102.54 | 97.43 | 574875
2026-07-04 | 16:00 | tsv_history_import | 360.6 | 29.34 | 102.54 | 97.49 | 568125
2026-07-04 | 17:00 | tsv_history_import | 372 | 29.66 | 102.54 | 97.37 | 581625
2026-07-04 | 18:00 | tsv_history_import | 388.6 | 30.11 | 102.54 | 97.46 | 571500
2026-07-04 | 19:00 | tsv_history_import | 382.9 | 29.82 | 102.54 | 97.67 | 547875
2026-07-04 | 20:00 | tsv_history_import | 358.9 | 28.71 | 102.54 | 97.59 | 556875
2026-07-04 | 21:00 | tsv_history_import | 350.5 | 28.57 | 102.54 | 97.52 | 564750
2026-07-04 | 22:00 | tsv_history_import | 337.6 | 28.04 | 102.54 | 97.45 | 572625
2026-07-04 | 23:00 | tsv_backfill | 359.6 | 29 | 102.54 | 97.5 | 567000
2026-07-05 | 00:00 | tsv_history_import | 319 | 27.38 | 102.54 | 97.25 | 595125
2026-07-05 | 01:00 | tsv_history_import | 318.1 | 27.58 | 106.37 | 97.38 | 1011375
2026-07-05 | 02:00 | tsv_history_import | 314.8 | 27.3 | 106.37 | 97.26 | 1024875
2026-07-05 | 03:00 | tsv_history_import | 308.8 | 27.26 | 106.37 | 97.27 | 1023750
2026-07-05 | 04:00 | tsv_history_import | 292.3 | 26.8 | 106.37 | 97.28 | 1022625
2026-07-05 | 05:00 | tsv_history_import | 289.6 | 26.6 | 106.37 | 97.32 | 1018125
2026-07-05 | 06:00 | tsv_history_import | 296.4 | 26.6 | 106.37 | 97.15 | 1037250
2026-07-05 | 06:53 | ebi_xps_import | 302.8 | 26.6 | 107.58 | 97.69 | 1112625
2026-07-05 | 07:00 | tsv_history_import | 302.5 | 26.6 | 107.72 | 97.23 | 1180125
2026-07-05 | 08:00 | tsv_history_import | 301 | 26.6 | 108.77 | 101 | 874125
2026-07-05 | 08:03 | ebi_xps_import | 292.2 | 26.6 | 112.53 | 101.98 | 1186875
2026-07-05 | 09:00 | tsv_history_import | 290.8 | 26.6 | 111.44 | 101.56 | 1111500
2026-07-05 | 10:00 | tsv_history_import | 293.6 | 26.71 | 110.65 | 101.18 | 1065375
2026-07-05 | 11:00 | tsv_history_import | 308.5 | 27.1 | 111.62 | 101.44 | 1145250
2026-07-05 | 12:00 | tsv_history_import | 309.1 | 27.1 | 110.51 | 101.08 | 1060875
2026-07-05 | 12:06 | ebi_xps_import | 308.2 | 27.1 | 112.72 | 102.07 | 1198125
2026-07-05 | 13:00 | tsv_history_import | 314.2 | 27.1 | 111.4 | 101.36 | 1129500
2026-07-05 | 14:00 | tsv_history_import | 314.2 | 27.25 | 111.62 | 101.33 | 1157625
2026-07-05 | 14:07 | ebi_xps_import | 318.1 | 27.84 | 107.49 | 100.02 | 840375
2026-07-05 | 15:00 | tsv_history_import | 324.5 | 28.28 | 110.26 | 101.37 | 1000125
2026-07-05 | 16:00 | tsv_history_import | 326.9 | 28.53 | 108 | 101.67 | 712125
2026-07-05 | 17:00 | tsv_history_import | 324.6 | 28.53 | 109.35 | 101.94 | 833625
2026-07-05 | 18:00 | tsv_history_import | 337.7 | 29.23 | 107.58 | 101.93 | 635625
2026-07-05 | 19:00 | tsv_history_import | 338.6 | 29.23 | 107.58 | 101.83 | 646875
2026-07-05 | 20:00 | tsv_history_import | 339.5 | 29.23 | 107.58 | 101.89 | 640125
2026-07-05 | 21:00 | tsv_history_import | 327.1 | 28.63 | 107.58 | 101.98 | 630000
2026-07-05 | 22:00 | tsv_history_import | 313.7 | 28.17 | 109.77 | 101.74 | 903375
2026-07-05 | 23:00 | tsv_backfill | 325.4 | 28.63 | 107.58 | 102.26 | 598500
2026-07-06 | 00:00 | tsv_history_import | 289.9 | 27.16 | 109.68 | 101.89 | 876375
2026-07-06 | 01:00 | tsv_history_import | 282.1 | 26.97 | 111.65 | 101.71 | 1118250
2026-07-06 | 02:00 | tsv_history_import | 290.1 | 26.73 | 111.83 | 101.71 | 1138500
2026-07-06 | 03:00 | tsv_history_import | 210.3 | 26.02 | 112.53 | 102.4 | 1139625
2026-07-06 | 04:00 | tsv_history_import | 208.1 | 26.02 | 112.53 | 102.58 | 1119375
2026-07-06 | 05:00 | tsv_history_import | 209.7 | 26.02 | 112.53 | 102.43 | 1136250
2026-07-06 | 06:00 | tsv_history_import | 216.8 | 26.4 | 112.53 | 102.45 | 1134000
2026-07-06 | 07:00 | tsv_history_import | 221.7 | 26.66 | 112.53 | 102.44 | 1135125
2026-07-06 | 07:10 | ebi_xps_import | 222.6 | 26.66 | 112.53 | 102.92 | 1081125
2026-07-06 | 08:00 | tsv_history_import | 244.5 | 26.66 | 112.45 | 102.29 | 1143000
2026-07-06 | 08:45 | ebi_xps_import | 258 | 26.66 | 112.44 | 101.33 | 1249875
2026-07-06 | 09:00 | tsv_history_import | 256.5 | 26.66 | 111.32 | 101.8 | 1071000
2026-07-06 | 10:00 | tsv_history_import | 257.1 | 26.66 | 111.77 | 101.69 | 1134000
2026-07-06 | 11:00 | tsv_history_import | 252.4 | 26.66 | 111.3 | 101.84 | 1064250
2026-07-06 | 12:00 | tsv_history_import | 236.8 | 26.66 | 110.87 | 103.38 | 842625
2026-07-06 | 12:31 | ebi_xps_import | 228.6 | 26.66 | 122.6 | 111.04 | 1300500
2026-07-06 | 12:44 | ebi_xps_import | 242 | 26.66 | 122.6 | 110.66 | 1343250
2026-07-06 | 13:00 | tsv_history_import | 235.3 | 26.73 | 120.42 | 110.73 | 1090125
2026-07-06 | 14:00 | tsv_history_import | 279.3 | 27.93 | 116.51 | 107.36 | 1029375
2026-07-06 | 15:00 | tsv_backfill | 259.9 | 27.15 | 127.98 | 117.11 | 1222875
2026-07-06 | 16:00 | tsv_history_import | 323.5 | 30.04 | 126.2 | 116.16 | 1129500
2026-07-06 | 17:00 | tsv_history_import | 308.3 | 29.9 | 124.84 | 116.03 | 991125
2026-07-06 | 18:00 | tsv_history_import | 317.7 | 29.94 | 124.91 | 115.89 | 1014750
2026-07-06 | 19:00 | tsv_history_import | 298.7 | 30.46 | 123.08 | 116.37 | 754875
2026-07-06 | 20:00 | tsv_history_import | 309.9 | 30.17 | 123.08 | 116.43 | 748125
2026-07-06 | 21:00 | tsv_history_import | 303.5 | 29.6 | 128.1 | 117.54 | 1188000
2026-07-06 | 22:00 | tsv_history_import | 298.1 | 28.94 | 128.27 | 118.03 | 1152000
2026-07-06 | 23:00 | tsv_backfill | 305.4 | 29.68 | 128.27 | 118.69 | 1077750
2026-07-07 | 00:00 | tsv_history_import | 251.8 | 27.84 | 128.27 | 118.37 | 1113750
2026-07-07 | 01:00 | tsv_history_import | 222.5 | 27.25 | 127.98 | 118.75 | 1038375
2026-07-07 | 02:00 | tsv_history_import | 216 | 26.78 | 127.98 | 118.82 | 1030500
2026-07-07 | 03:00 | tsv_history_import | 184.2 | 26.35 | 127.98 | 119.07 | 1002375
2026-07-07 | 04:00 | tsv_history_import | 172.4 | 25.78 | 127.98 | 119.3 | 976500
2026-07-07 | 05:00 | tsv_history_import | 169.9 | 25.78 | 127.98 | 119.42 | 963000
2026-07-07 | 06:00 | tsv_history_import | 147.1 | 25.28 | 127.98 | 119.23 | 984375
2026-07-07 | 07:00 | tsv_history_import | 145.1 | 25.18 | 127.98 | 119.27 | 979875
2026-07-07 | 07:23 | ebi_xps_import | 167.7 | 25.18 | 128.36 | 120.37 | 898875
2026-07-07 | 08:00 | tsv_history_import | 197.5 | 25.67 | 131.58 | 121.02 | 1188000
2026-07-07 | 09:00 | tsv_history_import | 240.3 | 27.25 | 132.16 | 121.45 | 1204875
2026-07-07 | 10:00 | tsv_history_import | 275.3 | 29.29 | 132.51 | 121.84 | 1200375
2026-07-07 | 11:00 | tsv_history_import | 318.7 | 31.47 | 131.6 | 121.99 | 1081125
2026-07-07 | 12:00 | tsv_history_import | 409 | 32.41 | 130.65 | 121.52 | 1027125
2026-07-07 | 13:00 | tsv_history_import | 396.2 | 31.47 | 128.36 | 120.87 | 842625
2026-07-07 | 14:00 | tsv_history_import | 389.1 | 32.04 | 129.14 | 121.09 | 905625
2026-07-07 | 15:00 | tsv_history_import | 391 | 32.43 | 129.39 | 121.19 | 922500
2026-07-07 | 16:00 | tsv_history_import | 394 | 32.34 | 128.46 | 121.3 | 805500
2026-07-07 | 17:00 | tsv_history_import | 389.3 | 32.31 | 128.46 | 121.53 | 779625
2026-07-07 | 18:00 | tsv_history_import | 385.3 | 32.31 | 128.46 | 121.65 | 766125
2026-07-07 | 19:00 | tsv_history_import | 378.1 | 31.87 | 128.46 | 121.52 | 780750
2026-07-07 | 20:00 | tsv_history_import | 351.6 | 31.32 | 128.46 | 121.86 | 742500
2026-07-07 | 21:00 | tsv_history_import | 333.7 | 30.74 | 128.63 | 121.93 | 753750
2026-07-07 | 22:00 | tsv_history_import | 322.8 | 30.04 | 132.26 | 122.35 | 1114875
2026-07-07 | 23:00 | tsv_history_import | 324.5 | 30.19 | 131.35 | 121.88 | 1065375
2026-07-08 | 00:00 | tsv_history_import | 307.7 | 29.51 | 132.49 | 122.08 | 1171125
2026-07-08 | 01:00 | tsv_history_import | 300.1 | 29.07 | 131.61 | 122.11 | 1068750
2026-07-08 | 02:00 | tsv_history_import | 296.4 | 29.07 | 132.23 | 121.9 | 1162125
2026-07-08 | 03:00 | tsv_history_import | 297.1 | 29.07 | 131.36 | 121.65 | 1092375
2026-07-08 | 04:00 | tsv_history_import | 286.7 | 28.46 | 132.18 | 121.76 | 1172250
2026-07-08 | 05:00 | tsv_history_import | 278.8 | 28.33 | 132.99 | 121.86 | 1252125
2026-07-08 | 06:00 | tsv_history_import | 282.9 | 28.03 | 131.95 | 121.52 | 1173375
2026-07-08 | 07:00 | tsv_history_import | 275.7 | 27.66 | 133.14 | 121.59 | 1299375
2026-07-08 | 08:00 | tsv_history_import | 289.8 | 28.43 | 133.03 | 121.75 | 1269000
2026-07-08 | 09:00 | tsv_history_import | 312.1 | 29.34 | 133.56 | 121.98 | 1302750
2026-07-08 | 10:00 | tsv_history_import | 337.8 | 30.06 | 132.37 | 122.21 | 1143000
2026-07-08 | 11:00 | tsv_history_import | 392.2 | 31.09 | 130.33 | 121.61 | 981000
2026-07-08 | 12:00 | tsv_history_import | 416.3 | 32.13 | 128.46 | 121.37 | 797625
2026-07-08 | 13:00 | tsv_history_import | 396.8 | 32.2 | 128.46 | 121.79 | 750375
2026-07-08 | 14:00 | tsv_history_import | 395.4 | 32.21 | 128.46 | 121.54 | 778500
2026-07-08 | 15:00 | tsv_history_import | 410.7 | 32.7 | 128.46 | 121.93 | 734625
2026-07-08 | 16:00 | tsv_history_import | 403.2 | 31.96 | 128.46 | 122.12 | 713250
2026-07-08 | 17:00 | tsv_history_import | 409.4 | 32.26 | 128.46 | 122.13 | 712125
2026-07-08 | 18:00 | tsv_history_import | 400.1 | 32.39 | 128.46 | 122.2 | 704250
2026-07-08 | 19:00 | tsv_history_import | 376.7 | 31.69 | 128.46 | 122.51 | 669375
2026-07-08 | 20:00 | tsv_history_import | 359.3 | 31.35 | 128.46 | 122.69 | 649125
2026-07-08 | 21:00 | tsv_history_import | 336.3 | 31.27 | 128.46 | 122.56 | 663750
2026-07-08 | 22:00 | tsv_history_import | 312.2 | 31.83 | 128.46 | 123.49 | 559125
2026-07-08 | 23:00 | tsv_history_import | 309.1 | 31.92 | 128.46 | 124.01 | 500625
2026-07-09 | 00:00 | tsv_history_import | 294.3 | 31.19 | 128.46 | 123.97 | 505125
2026-07-09 | 01:00 | tsv_history_import | 286.2 | 30.64 | 132.61 | 123.68 | 1004625
2026-07-09 | 02:00 | tsv_history_import | 274.1 | 30.23 | 133.56 | 123.61 | 1119375
2026-07-09 | 03:00 | tsv_history_import | 285.7 | 29.94 | 133.56 | 123.19 | 1166625
2026-07-09 | 04:00 | tsv_history_import | 279.8 | 29.35 | 133.56 | 122.95 | 1193625
2026-07-09 | 05:00 | tsv_history_import | 265.3 | 28.77 | 133.56 | 122.93 | 1195875
2026-07-09 | 06:00 | tsv_history_import | 254.7 | 28.15 | 133.56 | 122.75 | 1216125
2026-07-09 | 07:00 | tsv_history_import | 268.1 | 28.09 | 132.67 | 122.51 | 1143000
2026-07-09 | 08:00 | tsv_history_import | 300.5 | 28.44 | 133.46 | 122.18 | 1269000
2026-07-09 | 09:00 | tsv_history_import | 343.8 | 29.66 | 133.11 | 121.85 | 1266750
2026-07-09 | 10:00 | tsv_history_import | 382.6 | 31.09 | 131.49 | 121.62 | 1110375
2026-07-09 | 11:00 | tsv_history_import | 423.6 | 32.46 | 129.75 | 121.8 | 894375
2026-07-09 | 12:00 | tsv_history_import | 421.5 | 32.43 | 130.1 | 121.89 | 923625
2026-07-09 | 13:00 | tsv_history_import | 404.5 | 32.75 | 128.65 | 122.19 | 726750
2026-07-09 | 14:00 | tsv_history_import | 407.6 | 32.89 | 128.65 | 122.42 | 700875
2026-07-09 | 15:00 | tsv_history_import | 411.2 | 32.67 | 128.65 | 122.49 | 693000
2026-07-09 | 16:00 | tsv_history_import | 279.9 | 29.06 | 133.24 | 123.62 | 1082250
2026-07-09 | 17:00 | tsv_history_import | 310.4 | 30.19 | 130.59 | 123.29 | 821250
2026-07-09 | 18:00 | tsv_history_import | 351.4 | 31.08 | 129.11 | 122.6 | 732375
2026-07-09 | 19:00 | tsv_history_import | 365 | 31.08 | 128.94 | 122.04 | 776250
2026-07-09 | 20:00 | tsv_history_import | 368.4 | 30.84 | 128.94 | 122.18 | 760500
2026-07-09 | 21:00 | tsv_history_import | 350.6 | 30.39 | 130.47 | 122.2 | 930375
2026-07-09 | 22:00 | tsv_history_import | 333.7 | 29.76 | 129.89 | 122 | 887625
2026-07-09 | 23:00 | tsv_history_import | 334.4 | 29.94 | 131.76 | 121.96 | 1102500
2026-07-10 | 00:00 | tsv_history_import | 319.8 | 29.49 | 131.9 | 122.02 | 1111500
2026-07-10 | 01:00 | tsv_history_import | 307.2 | 28.94 | 133.26 | 121.9 | 1278000
2026-07-10 | 02:00 | tsv_history_import | 305.4 | 28.94 | 132.43 | 121.87 | 1188000
2026-07-10 | 03:00 | tsv_history_import | 299 | 28.46 | 132 | 121.86 | 1140750
2026-07-10 | 04:00 | tsv_history_import | 287.7 | 28.32 | 131.48 | 121.56 | 1116000
2026-07-10 | 05:00 | tsv_history_import | 270.9 | 27.67 | 131.9 | 121.71 | 1146375
2026-07-10 | 06:00 | tsv_history_import | 271.8 | 27.6 | 133.17 | 121.99 | 1257750
2026-07-10 | 07:00 | tsv_history_import | 282.3 | 27.6 | 131.8 | 121.73 | 1132875
2026-07-10 | 08:00 | tsv_history_import | 283.5 | 27.6 | 132.34 | 121.7 | 1197000
2026-07-10 | 09:00 | tsv_history_import | 272.6 | 27.94 | 131.9 | 121.64 | 1154250
2026-07-10 | 10:00 | tsv_history_import | 281 | 28.26 | 132.8 | 121.79 | 1238625
2026-07-10 | 11:00 | tsv_history_import | 298.2 | 28.45 | 131.84 | 121.7 | 1140750
2026-07-10 | 12:00 | tsv_history_import | 330.2 | 29.28 | 131.42 | 121.43 | 1123875
2026-07-10 | 13:00 | tsv_history_import | 363.1 | 30.56 | 129.77 | 121.46 | 934875
2026-07-10 | 14:00 | tsv_history_import | 355.1 | 30.37 | 128.56 | 121.15 | 833625
2026-07-10 | 15:00 | tsv_history_import | 363.3 | 30.44 | 128.56 | 121.25 | 822375
2026-07-10 | 16:00 | tsv_history_import | 381.4 | 31.25 | 128.56 | 121.31 | 815625
2026-07-10 | 17:00 | tsv_history_import | 384.3 | 31.68 | 128.56 | 121.49 | 795375
2026-07-10 | 18:00 | tsv_history_import | 352.6 | 31.3 | 128.56 | 121.99 | 739125
2026-07-10 | 19:00 | tsv_history_import | 351.7 | 31.14 | 129.15 | 122.26 | 775125
2026-07-10 | 20:00 | tsv_history_import | 276.8 | 28.07 | 133.65 | 122.68 | 1234125
2026-07-10 | 21:00 | tsv_history_import | 283.7 | 27.95 | 133.4 | 122.53 | 1222875
2026-07-10 | 22:00 | tsv_history_import | 295.7 | 28.26 | 132.73 | 122.34 | 1168875
2026-07-10 | 23:00 | tsv_history_import | 299.7 | 28.26 | 132.45 | 122.06 | 1168875
2026-07-11 | 00:00 | tsv_history_import | 301.6 | 28.26 | 132.45 | 121.76 | 1202625
2026-07-11 | 01:00 | tsv_history_import | 278.2 | 27.65 | 132.28 | 122.07 | 1148625
2026-07-11 | 02:00 | tsv_history_import | 276.2 | 27.49 | 132.21 | 121.81 | 1170000
2026-07-11 | 03:00 | tsv_history_import | 257.5 | 27.13 | 133.48 | 121.74 | 1320750
2026-07-11 | 04:00 | tsv_history_import | 251.4 | 26.84 | 133.14 | 121.8 | 1275750
2026-07-11 | 05:00 | tsv_history_import | 238.6 | 26.61 | 133.14 | 121.98 | 1255500
2026-07-11 | 06:00 | tsv_history_import | 227 | 26.21 | 133.37 | 121.76 | 1306125
2026-07-11 | 07:00 | tsv_history_import | 207.1 | 26.21 | 133.4 | 121.97 | 1285875
2026-07-11 | 08:00 | tsv_history_import | 228.7 | 26.21 | 133.75 | 121.83 | 1341000
2026-07-11 | 09:00 | tsv_history_import | 246.9 | 26.23 | 133.11 | 121.49 | 1307250
2026-07-11 | 10:00 | tsv_history_import | 275.7 | 27.48 | 131.04 | 121.16 | 1111500
2026-07-11 | 11:00 | tsv_history_import | 325.7 | 29.04 | 130.84 | 120.88 | 1120500
2026-07-11 | 12:00 | tsv_history_import | 368 | 30.13 | 131.98 | 121.23 | 1209375
2026-07-11 | 13:00 | tsv_history_import | 385.4 | 30.56 | 128.83 | 120.62 | 923625
2026-07-11 | 14:00 | tsv_history_import | 342.9 | 30.31 | 128.65 | 120.88 | 874125
2026-07-11 | 15:00 | tsv_history_import | 345.7 | 30.77 | 128.65 | 121.16 | 842625
2026-07-11 | 16:00 | tsv_history_import | 337 | 30.43 | 128.65 | 121.03 | 857250
2026-07-11 | 17:00 | tsv_history_import | 320.4 | 30.25 | 128.65 | 121.15 | 843750
2026-07-11 | 18:00 | tsv_history_import | 309.1 | 29.72 | 130.01 | 121.17 | 994500
2026-07-11 | 19:00 | tsv_history_import | 309.9 | 29.72 | 128.65 | 120.83 | 879750
2026-07-11 | 20:00 | tsv_history_import | 310.9 | 29.72 | 128.65 | 121 | 860625
2026-07-11 | 21:00 | tsv_history_import | 309.4 | 29.51 | 130.18 | 121.61 | 964125
2026-07-11 | 22:00 | tsv_history_import | 293.4 | 28.85 | 131.84 | 121.63 | 1148625
2026-07-11 | 23:00 | tsv_history_import | 271.3 | 28.79 | 132.45 | 121.87 | 1190250
2026-07-12 | 00:00 | tsv_history_import | 276.3 | 28.3 | 132.6 | 121.98 | 1194750
2026-07-12 | 01:00 | tsv_history_import | 234.2 | 27.48 | 132.92 | 121.8 | 1251000
2026-07-12 | 02:00 | tsv_history_import | 219.2 | 26.87 | 132.97 | 121.74 | 1263375
2026-07-12 | 03:00 | tsv_history_import | 213.9 | 27.07 | 133.05 | 122.16 | 1225125
2026-07-12 | 04:00 | tsv_history_import | 181 | 26.45 | 133.46 | 122.15 | 1272375
2026-07-12 | 05:00 | tsv_history_import | 199 | 25.82 | 133.2 | 121.6 | 1305000
2026-07-12 | 06:00 | tsv_history_import | 186.1 | 25.36 | 133.13 | 121.9 | 1263375
2026-07-12 | 07:00 | tsv_history_import | 183.7 | 25.13 | 133.56 | 121.1 | 1401750
2026-07-12 | 08:00 | tsv_history_import | 199.8 | 25.8 | 133.02 | 121.33 | 1315125
2026-07-12 | 09:00 | tsv_history_import | 247.9 | 27.41 | 133.46 | 121.08 | 1392750
2026-07-12 | 10:00 | tsv_history_import | 262.6 | 28.99 | 132.02 | 121.13 | 1225125
2026-07-12 | 11:00 | tsv_history_import | 304 | 30.08 | 132.3 | 121.45 | 1220625
2026-07-12 | 12:00 | tsv_history_import | 322.5 | 31.23 | 129.53 | 121.48 | 905625
2026-07-12 | 13:00 | tsv_history_import | 373.1 | 30.62 | 129.11 | 120.35 | 985500
2026-07-12 | 14:00 | tsv_history_import | 345.1 | 30.5 | 129.03 | 120.49 | 960750
2026-07-12 | 15:00 | tsv_history_import | 310.2 | 30.19 | 129.43 | 120.89 | 960750
2026-07-12 | 16:00 | tsv_history_import | 317.1 | 30.19 | 129.72 | 121.08 | 972000
2026-07-12 | 17:00 | tsv_history_import | 317 | 30.19 | 129.72 | 121.01 | 979875
2026-07-12 | 18:00 | tsv_history_import | 314.8 | 30.03 | 129.74 | 121 | 983250
2026-07-12 | 19:00 | tsv_history_import | 307.6 | 29.57 | 129.9 | 121.04 | 996750
2026-07-12 | 20:00 | tsv_history_import | 307.4 | 29.57 | 129.98 | 121.03 | 1006875
2026-07-12 | 21:00 | tsv_history_import | 288.7 | 29.08 | 130.04 | 121.06 | 1010250
2026-07-12 | 22:00 | tsv_history_import | 272.3 | 28.64 | 132.98 | 121.67 | 1272375
2026-07-12 | 23:00 | tsv_history_import | 226.1 | 27.95 | 132.98 | 121.83 | 1254375
2026-07-13 | 00:00 | tsv_history_import | 241.8 | 27.95 | 132.98 | 122.03 | 1231875
2026-07-13 | 01:00 | tsv_history_import | 197.1 | 27.17 | 130.67 | 122.39 | 931500
2026-07-13 | 02:00 | tsv_history_import | 214.8 | 26.64 | 130.67 | 122.07 | 967500
2026-07-13 | 03:00 | tsv_history_import | 213.4 | 26.14 | 130.67 | 122.01 | 974250
2026-07-13 | 04:00 | tsv_history_import | 204.6 | 25.77 | 130.67 | 121.67 | 1012500
2026-07-13 | 05:00 | tsv_history_import | 202.8 | 25.59 | 130.67 | 121.84 | 993375
2026-07-13 | 06:00 | tsv_history_import | 196.2 | 25.4 | 130.67 | 121.51 | 1030500
2026-07-13 | 07:00 | tsv_history_import | 204.2 | 25.52 | 130.67 | 121.78 | 1000125
2026-07-13 | 08:00 | tsv_history_import | 254.8 | 25.94 | 130.67 | 120.88 | 1101375
2026-07-13 | 09:00 | tsv_history_import | 252.8 | 27.55 | 130.87 | 121.4 | 1065375
2026-07-13 | 10:00 | tsv_history_import | 315.1 | 29.36 | 131.72 | 121.06 | 1199250
2026-07-13 | 11:00 | tsv_history_import | 337.8 | 30.23 | 132.09 | 121.21 | 1224000
2026-07-13 | 12:00 | tsv_history_import | 350.4 | 31.86 | 132.26 | 121.8 | 1176750
2026-07-13 | 13:00 | tsv_history_import | 352.6 | 31.29 | 130.16 | 121.13 | 1015875
2026-07-13 | 14:00 | tsv_history_import | 328.3 | 30.36 | 112.78 | 108.11 | 525375
2026-07-13 | 15:00 | tsv_history_import | 322.7 | 30.91 | 112.53 | 108.71 | 429750
2026-07-13 | 16:00 | tsv_history_import | 394.9 | 31.35 | 112.53 | 108.47 | 456750
2026-07-13 | 17:00 | tsv_history_import | 393.4 | 31.7 | 112.53 | 108.53 | 450000
2026-07-13 | 18:00 | tsv_history_import | 392.6 | 31.7 | 112.53 | 108.52 | 451125
2026-07-13 | 19:00 | tsv_history_import | 391 | 31.7 | 112.53 | 108.63 | 438750
2026-07-13 | 20:00 | tsv_history_import | 377 | 31.51 | 112.53 | 108.75 | 425250
2026-07-13 | 21:00 | tsv_history_import | 351 | 30.72 | 112.78 | 108.44 | 488250
2026-07-13 | 22:00 | tsv_history_import | 329 | 30.1 | 119.62 | 112.73 | 775125
2026-07-13 | 23:00 | tsv_history_import | 322 | 29.79 | 122.69 | 115.86 | 768375
2026-07-14 | 00:00 | tsv_history_import | 314.1 | 29.35 | 126.26 | 117.18 | 1021500
2026-07-14 | 01:00 | tsv_history_import | 316.5 | 28.85 | 124.81 | 117.59 | 812250
2026-07-14 | 02:00 | tsv_history_import | 317.7 | 29.07 | 124.81 | 118.2 | 743625
2026-07-14 | 03:00 | tsv_history_import | 317.4 | 29.16 | 124.81 | 119.37 | 612000
2026-07-14 | 04:00 | tsv_history_import | 306.6 | 28.77 | 128.81 | 120.01 | 990000
2026-07-14 | 05:00 | tsv_history_import | 293.9 | 28.81 | 132.48 | 121.3 | 1257750
2026-07-14 | 06:00 | tsv_history_import | 280 | 28.3 | 132.79 | 121.88 | 1227375
2026-07-14 | 07:00 | tsv_history_import | 279.5 | 28.3 | 132.79 | 122.11 | 1201500
2026-07-14 | 08:00 | tsv_history_import | 278.9 | 27.76 | 132.7 | 122.18 | 1183500
2026-07-14 | 09:00 | tsv_history_import | 293 | 28.06 | 127.69 | 119.63 | 906750
2026-07-14 | 10:00 | tsv_history_import | 327.9 | 29.11 | 126.13 | 116.1 | 1128375
2026-07-14 | 11:00 | tsv_history_import | 362.4 | 30.05 | 121.41 | 112.31 | 1023750
2026-07-14 | 12:00 | tsv_history_import | 391.6 | 31.09 | 112.44 | 104.23 | 923625
2026-07-14 | 13:00 | tsv_history_import | 414.2 | 32.16 | 107.01 | 99.19 | 879750
2026-07-14 | 14:00 | tsv_history_import | 425.3 | 32.34 | 95.96 | 90.46 | 618750
2026-07-14 | 15:00 | tsv_history_import | 423.3 | 32.5 | 87.14 | 85.79 | 151875
2026-07-14 | 16:00 | tsv_history_import | 411.4 | 32.61 | 87.14 | 85.87 | 142875
2026-07-14 | 17:00 | tsv_history_import | 418.7 | 33.14 | 87.14 | 86.26 | 99000
2026-07-14 | 18:00 | tsv_history_import | 421.8 | 33.18 | 87.14 | 85.98 | 130500
2026-07-14 | 19:00 | tsv_history_import | 411.9 | 32.79 | 87.14 | 86.04 | 123750
2026-07-14 | 20:00 | tsv_history_import | 403.9 | 32.31 | 87.14 | 85.96 | 132750
2026-07-14 | 21:00 | tsv_history_import | 387 | 31.51 | 87.14 | 85.65 | 167625
2026-07-14 | 22:00 | tsv_history_import | 385.6 | 31.27 | 94.45 | 89.73 | 531000
2026-07-14 | 23:00 | tsv_history_import | 364.4 | 30.68 | 100.33 | 95.17 | 580500
2026-07-15 | 00:00 | tsv_history_import | 355 | 30.3 | 105.54 | 98.54 | 787500
2026-07-15 | 01:00 | tsv_history_import | 367 | 30.29 | 106.94 | 102.01 | 554625
2026-07-15 | 02:00 | tsv_history_import | 368.2 | 30.15 | 112.7 | 104.81 | 887625
2026-07-15 | 03:00 | tsv_history_import | 351.2 | 29.69 | 117.57 | 107.81 | 1098000
2026-07-15 | 04:00 | tsv_history_import | 351.6 | 29.33 | 120.39 | 112.17 | 924750
2026-07-15 | 05:00 | tsv_history_import | 344.1 | 28.99 | 127.34 | 118.14 | 1035000
2026-07-15 | 06:00 | tsv_history_import | 333.1 | 28.7 | 131.2 | 120.99 | 1148625
2026-07-15 | 07:00 | tsv_history_import | 322.8 | 28.41 | 131.62 | 121.13 | 1180125

## Daily
Date | Wx High °F | Wx Low °F | Wx Avg °F | Avg Enthalpy | Peak Enthalpy | CDD | Plant Peak Tons | Plant Avg Tons | Ton-Hours | kWh | kW/ton | Peak RLA % | Cond ΔT avg | BMS Calc Load max | Heat Loop BTU/h avg | Water Total gal | Tower Makeup gal | Tower Blowdown gal | COC (calc) | Gal/Ton-hr
2026-06-09 | 83.4 | 68.9 | 75.2 | 34.9 | 38.1 | 10.2 | 443.1 | 346.8 | 8565 | 4499 | 0.53 | 88 | 8 | 370.2 | 822375 | 12410 | 10310 | 1600 | 6.4 | 1.2
2026-06-10 | 90.4 | 71.1 | 78.8 | 37 | 39.7 | 13.8 | 465.5 | 411.5 | 9964 | 4787 | 0.54 | 90 | 7.4 | 418.6 | 917625 | 17600 | 14410 | 820 | 17.6 | 1.45
2026-06-11 | 87.5 | 68.8 | 79.1 | 35 | 37.5 | 14.1 | 393.3 | 370.1 | 8867 | 4587 | 0.52 | 70.1 | 6.3 | 420.7 | 545625 | 15130 | 12620 | 415 | 30.4 | 1.42
2026-06-12 | 80.6 | 68.8 | 74.5 | 29.9 | 35.4 | 9.5 | 351 | 249.3 | 5780 | 3116 | 0.54 | 77 | 6.1 | 282.4 | 948375
2026-06-13 | 88.4 | 64.3 | 77.6 | 28.7 | 30.6 | 12.6 | 206.6 | 175.5 | 4247 | 2477 | 0.58 | 86.2 | 6.7 | 286.6 | 1048500 | 24910 | 10330 | 4388 | 2.4 | 2.43
2026-06-14 | 78.1 | 60.3 | 69 | 29.6 | 34.3 | 4 | 216.6 | 172.6 | 4125 | 2470 | 0.6 | 92.3 | 6 | 250.5 | 1189875
2026-06-15 | 70.6 | 51.4 | 62 | 22.6 | 25.2 | 0 | 112 | 95.4 | 2322 | 1528 | 0.66 | 52.3 | 4.6 | 160.8 | 1203000 | 14270 | 5770 | 2462 | 2.3 | 2.48
2026-06-16 | 76.6 | 57.4 | 66.4 | 24.1 | 26.7 | 1.4 | 129.4 | 107.9 | 2601 | 1673 | 0.64 | 56.1 | 5 | 189.3 | 1175400 | 6270 | 5130 | 1438 | 3.6 | 1.97
2026-06-17 | 75 | 57.9 | 64.7 | 25.9 | 29.4 | 0 | 122 | 111.5 | 2624 | 1679 | 0.65 | 54.8 | 5.1 | 183.6 | 1324500 | 1480
2026-06-18 | 70.2 | 62 | 66.7 | 27.7 | 31.1 | 1.7 | 139.4 | 125 | 3040 | 1869 | 0.63 | 60 | 5.3 | 227.6 | 978375 | 13200 | 11720 | 7434 | 1.6 | 3.86
2026-06-19 | 73.9 | 56.7 | 65.8 | 24.5 | 26.2 | 0.8 | 149.3 | 83 | 1902 | 1671 | 0.9 | 56 | 5.3 | 178 | 998250 | 6580 | 5520 | 2667 | 2.1 | 2.9
2026-06-20 | 75.7 | 58.1 | 66.8 | 25.1 | 28.7 | 1.8 | 129.4 | 112 | 2700 | 1696 | 0.63 | 56.3 | 5 | 175.6 | 1066125
2026-06-21 | 77.5 | 56.5 | 67.1 | 26.2 | 29.4 | 2.1 | 166.8 | 131.5 | 3209 | 2102 | 0.66 | 75.5 | 5.6 | 206 | 1398656
2026-06-22 | 73.7 | 59.9 | 65.9 | 26.7 | 28.9 | 0.9 | 156.8 | 138.1 | 3263 | 2102 | 0.64 | 72.3 | 6.1 | 199.5 | 1309500 | 39880 | 9697 | 5064 | 1.9 | 2.97
2026-06-23 | 75.2 | 55.6 | 65.9 | 24.9 | 27.6 | 0.9 | 141.9 | 118 | 2712 | 1804 | 0.66 | 62.6 | 5.2 | 183.2 | 1428000
2026-06-24 | 73.9 | 54.4 | 65.2 | 25.9 | 27.9 | 0.2 | 124.5 | 112 | 2706 | 1771 | 0.66 | 55.2 | 5.2 | 174.6 | 1118250 | 7400 | 3100 | 350 | 8.9 | 1.15
2026-06-25 | 77.9 | 62.2 | 69 | 29.1 | 32.6 | 4 | 323.6 | 232.3 | 5775 | 3195 | 0.56 | 82.8 | 5.8 | 272.7 | 1181250 | 7280 | 6180 | 700 | 8.8 | 1.07
2026-06-26 | 72 | 58.6 | 66.3 | 28 | 29.5 | 1.3 | 194.2 | 174.8 | 4177 | 2047 | 0.49 | 72.2 | 7.5 | 215.7 | 1340250 | 10520 | 10100 | 4389 | 2.3 | 2.42
2026-06-27 | 78.4 | 60.6 | 69.6 | 28.6 | 31.1 | 4.6 | 174.2 | 165.1 | 3975 | 2117 | 0.53 | 70.8 | 6.2 | 257.4 | 1261125
2026-06-28 | 82.2 | 63.3 | 73.5 | 31.7 | 34.6 | 8.5 | 248.9 | 195 | 4762 | 2612 | 0.54 | 95 | 6.2 | 312.5 | 1116375
2026-06-29 | 90.9 | 67.4 | 79.6 | 34.6 | 39 | 14.6 | 388.3 | 304.9 | 7469 | 4253 | 0.57 | 90.3 | 6.5 | 376.9 | 366000 | 27120 | 8690 | 0 |  | 1.16
2026-06-30 | 97.1 | 76.5 | 86.7 | 40.3 | 42.1 | 21.7 | 400.8 | 371.7 | 8974 | 4970 | 0.55 | 75.7 | 6.7 | 418.8 | 328875 | 13280 | 12870 | 405 | 31.7 | 1.43
2026-07-01 | 99.1 | 75.3 | 88.6 | 39.8 | 42.5 | 23.6 | 420.7 | 382.1 | 9170 | 5134 | 0.56 | 81.4 | 6.7 | 464.3 | 467408 | 14850 | 14390 | 1634 | 8.8 | 1.57
2026-07-02 | 98.1 | 79.9 | 89.4 | 39.3 | 40.5 | 24.4 | 403.2 | 380 | 9153 | 5121 | 0.56 | 77.4 | 6.6 | 431 | 469583 | 16290 | 15990 | 3259 | 4.9 | 1.75
2026-07-03 | 98 | 73.9 | 84.7 | 37.9 | 40.4 | 19.7 | 405.7 | 362.6 | 8655 | 4802 | 0.55 | 76.3 | 6.3 | 451.4 | 483911 | 16280 | 16090 | 4066 | 4 | 1.86
2026-07-04 | 85.2 | 71.2 | 76.8 | 36 | 38.2 | 11.8 | 348.5 | 328.2 | 7906 | 4265 | 0.54 | 66.4 | 5.7 | 388.6 | 647351 | 13540 | 13180 | 2238 | 5.9 | 1.67
2026-07-05 | 77.8 | 70 | 72.8 | 35.2 | 36.6 | 7.8 | 328.6 | 318.2 | 7617 | 3942 | 0.52 | 60.7 | 5.5 | 339.5 | 942710 | 11690 | 11120 | 635 | 17.5 | 1.46
2026-07-06 | 80 | 65.2 | 72.2 | 31.3 | 33.8 | 7.2 | 291.2 | 211.6 | 5010 | 2806 | 0.59 | 91.2 | 7.1 | 323.5 | 1086629 | 10500 | 9960 | 2991 | 3.3 | 1.99
2026-07-07 | 84.7 | 64.4 | 75.2 | 31.8 | 36.5 | 10.2 | 405.7 | 281.7 | 6980 | 3664 | 0.52 | 90 | 7 | 409 | 966735 | 8940 | 8560 | 0 |  | 1.23
2026-07-08 | 87.8 | 68.5 | 78.4 | 34.4 | 36.7 | 13.4 | 385.8 | 316.1 | 7360 | 3675 | 0.5 | 70.2 | 6.2 | 416.3 | 930000 | 10190 | 9700 | 0 |  | 1.32
2026-07-09 | 89.9 | 70.4 | 79.3 | 34 | 36.4 | 14.3 | 380.8 | 312 | 7669 | 4211 | 0.55 | 99.8 | 7 | 423.6 | 967594 | 17000 | 16690 | 6050 | 2.8 | 2.18
2026-07-10 | 84.8 | 69.9 | 75.2 | 35.5 | 37.7 | 10.2 | 420.7 | 382.9 | 9245 | 4424 | 0.48 | 68.2 | 6.3 | 384.3 | 1072359 | 13130 | 12680 | 77 | 165.7 | 1.37
2026-07-11 | 85.4 | 65.4 | 75.4 | 32.5 | 36.3 | 10.4 | 375.9 | 306.2 | 7196 | 3773 | 0.54 | 58.1 | 5 | 385.4 | 1101422 | 12370 | 12040 | 2117 | 5.7 | 1.67
2026-07-12 | 85.5 | 63.4 | 75.2 | 30.5 | 34.6 | 10.2 | 405.7 | 227.3 | 5503 | 3152 | 0.57 | 87.8 | 6.8 | 373.1 | 1150781 | 13750 | 13490 | 5811 | 2.3 | 2.45
2026-07-13 | 92 | 63.6 | 78.6 | 32 | 37.3 | 13.6 | 400.8 | 294.6 | 7236 | 3861 | 0.53 | 99 | 6.7 | 394.9 | 838875
2026-07-14 | 96.5 | 71.3 | 84.1 | 37.3 | 42.8 | 19.1 | [7 empty] | 425.3 | 691266
2026-07-15 | 98 | 75 | 85.3 | 38.7 | 44.7 | 20.3 | [7 empty] | 368.2 | 952031
2026-07-16 | 89.6 | 71.2 | 79 | 31.4 | 35.5 | 14
2026-07-17 | 86.6 | 66.3 | 76.6 | 32.2 | 37.9 | 11.6